## Info
Tool for techno-economic analysis of integrating
data centre waste heat into district heating
Version 1.1 - October 2026
© e-think energy research, 2024 - 2026
Contact: office@e-think.ac.at
This tool is intended for purposes such as research and support in estimating costs and benefits of integrating waste heat in district heating.
Feedback is highly appreciated.
This tool has been developed within the Support DHC project funded by the EU LIFE Programme. It intends to provide a simple method to calculate the break-even heat price for waste heat from data centres. It allows the user to provide techno-economic information on technical equipment necessary to connect the DC with an existing district heating network (i.e. heat pump, booster technology and additional piping).
The user can also define a set of typical days with individual energy prices, temperature levels as well as heat demand and heat supply capacities and combine these typical days to a typical year, for which then the break-even calculation is done.
Note that all economic parameters in the tool are expressed in constant prices (e.g. EUR 2025).
It is assumed that all costs and prices increase at the same inflation rate over time.
The authors accept no responsibility for the topicality, accuracy, completeness or quality of the tool in general, or the results in particular.
A user manual accompanies the tool, explaining the structure of the workbook, the required input parameters, the calculation logic, and the interpretation of results. It is designed to help users apply the tool effectively and carry out preliminary feasibility assessments for waste heat integration projects.
This work is licensed under a Creative Commons CC BY 4.0 International License.
License-Text: https://spdx.org/licenses/CC-BY-4.0.html
Authors: Andreas Müller, Marcus Hummel, Andrea Frank-Stocker, Ardak Akhatova (e-think)
Reviewer: Thomas Pauschinger (AGFW)

## Content
Worksheets & Workflow
Project Setting | Specify the project techno-economic data regarding heat pump, booster, heat recovery system, etc.
Grid Costs | Calculate additional grid / piping costs to connect the data centre (DC) with the existing district heating (DH) network
Definition of Typical Day | Define typical days comprising a year and set their parameters such as heat demand & supply, temperature levels and energy prices for typical days
Definition of Typical Year | Combine "Typical Days" to define the "Typical Year": Define the share of the "Typical Days" on a "Typical Year"
Main Results - IRR DC Operator | Visualise the results with different contract types and cost shares, focusing on the waste heat recovery system at the DC plant side
Operation at Typical Day | Visualise the energy and cost profile of a selected typical day
Calculation IRR | Calculate the Internal Rate of Return (IRR)
Calculation Break-Even | Calculate the break-even waste heat price
Main Results Extended | Visualise the results with different contract types and cost shares for the entire system (waste heat recovery and heat utilisation)
Calculation of Typical Day | Determine the energy balance and economic parameters of each typical day
Calculation of Typical Year | Determine the energy balance and economic parameters for the typical year
Additional Information | Additional explanations of the parameters used in the calculations
TechKatalogGWPA | Technology sheet "Großwärmepumpe Abwärme (Kompressionswärmepumpe)" from Technology Catalogue for Heat Planning Germany
Change Log | Overview of changes between tool versions
Colour code:
Header
Item / unit
User input
Cell with formula
Go to content
Input - not used for calculation
Not used anymore: relevant for future works - do not change
Control cells
Check settings / input data, there might be some error
Go to content
The main calculation sheets in this workbook are secured with a password in order not to do unintended changes
PW: 1234

## Project Setting
Go to Content
| Colour Code | Header
Item / unit
User input
Cell with formula
Go to Content
Input - not used for calculation
Control cells
| Category | Sub-Category | Item | Unit |  |  | Description
HEAT PUMP AND BOOSTER SYSTEM INCLUDING HEAT EXCHANGER AND PIPING TO THE DH GRID (B2 - B3) | Heat pump |  | All monetary values are expressed in constant prices (e.g. EUR 2025) | [5 empty] | CONTRACTOR 1 / DH OPERATOR
Technical data
|  |  | Generating capacity | MW_th | 3 |  | Nominal capacity of heat pump (heat output, MW_th_nominal_out); this value should be based on the available heat from the data Centre (in the sheet "Definition of Typical Day" - Available waste heat (DC heat source) | Link to additional information / German translation
|  |  | Technical lifetime | Years | 20 |  | The typical lifetime of a water-to-water heat pump is between 15 and 25 years, depending on many factors. Average lifetime can thus be estimated as 20 years. | Link to additional information / German translation
|  |  | COP - nominal | [MW / MW] | 3 |  | COP at 90°C supply temperature under nominal temperature levels as defined below | Link to additional information / German translation
|  |  | Capacity of waste heat stream (MW) at nominal operation conditions | MW_th_nominal_in | 2 |  | This is the HP system capacity related to the waste heat stream (waste heat source). This capacity shall be in the order of magnitude of the waste heat energy source or the feed-in capacity of the district heating system. The difference between MW_th_in and MW_th (MW_th_nominal_out) is the electricity input. | Link to additional information / German translation
|  |  | Nominal temperature - heat pump source in | °C | 25 |  | Source-side inlet temperature: The temperature of the heat source fluid before it enters the evaporator. Nominal temperature for the selected heat pump (e.g. from specification sheets of the heat pump). The actual temperatur of the waste heat source shall be provided in the sheet >Definition of Typical Day<. | Link to additional information / German translation
|  |  | Nominal temperature - heat pump source out | °C | 28 |  | Source-side outlet temperature: The temperature of the heat source fluid after it has passed through the evaporator and given up heat to the refrigerant. Nominal temperature for the selected heat pump (e.g. from specification sheets). | Link to additional information / German translation
|  |  | Nominal temperature - heat pump sink out | °C | 90 |  | Sink-side outlet Temperature: The temperature of the heat sink fluid after it has passed through the condenser and absorbed heat from the refrigerant. Nominal temperature for the selected heat pump (e.g. from specification sheets). The actual temperatur of the heat sink (e.g. district heating network supply line temperature) shall be provided in the sheet >Definition of Typical Day<. | Link to additional information / German translation
|  |  | HEx 2: Heat exchanger (HP - district heating network) delta T | K | 3 |  | Temperature drop that occurs due to losses in the heat exchanger and heat pipe between the Heat Pump and the DH network. | Link to additional information / German translation
|  |  | HEx 1: Heat exchanger (HP - data centre cooling system) delta T | K | 3 |  | Temperature drop that occurs due to losses in the heat exchanger and heat pipe between the Heat Pump and the Data Centre Cooling System. | Link to additional information / German translation
|  |  | Nominal Temperature - Heat Pump Sink In | °C | 60 |  | Sink-side inlet Temperature: The temperature of the heat sink fluid before it enters the condenser. Nominal temperature for the selected heat pump (e.g. from specification sheets). The actual temperatur of the heat sink (e.g. district heating network return line temperature) shall be provided in the sheet >Definition of Typical Day<. | Link to additional information / German translation
|  |  | Upper temperature limit - Heat pump Sink Out | °C | 95 |  | If the heat pump sink temperature (district heating supply line temperature + delta T of HEx 2) exceed this limit, then the remaining temperature needs to be provided by the booster. | Link to additional information / German translation
|  |  | Exponent for capacity drop if temperature spread of sink decreases |  | 50% |  | Quantifies how sensitively the heat pump's heating capacity decreases when the temperature spread on the sink side (i.e. between sink outlet and inlet) becomes smaller. A higher exponent indicates a stronger reduction in capacity for small temperature spreads. If Zero, than no impact on capacity, if 1 then a reduction of temperature spread of heat sink reduces the capacity by the some ratio. Set value between 0 and 1. | Link to additional information / German translation
|  |  | S - Source | - | 0.02 | Check impact of settings on COP | Increase of COP per increasing degree of Heat Source In temperature as compared to 25°C. The impact of the settings on COP can be check at the bottom of this sheet. | Link to additional information / German translation
|  |  | S - Flow | - | 0.026 | Check impact of settings on COP | Decrease of COP per increasing degree of Heat Sink Out temperature (e.g. grid supply line) as compared to 90°C. The impact of the settings on COP can be check at the bottom of this sheet. | Link to additional information / German translation
|  |  | S - Return | - | 0 | Check impact of settings on COP | Increase of COP per increasing degree of Heat Sink In temperature (e.g. grid return line) as compared to 60°C. PLEASE READ ADDITIONAL NOTES | Link to additional information / German translation
|  |  | Share of heat loss in heat exchangers & pipes from HP output | % | 1 |  | The percentage of thermal energy lost between the heat pump’s output and the grid that lead to reduced heat supplied to the grid as compared to the nominal capacity. This includes losses due to inefficiencies in heat exchangers, as well as thermal losses in piping. | Link to additional information / German translation
Economic data
|  |  | Specific investment costs (equipment, installation) | EUR/kW_th | 1500 |  | The specific costs (i.e. expressed per unit of installed capacity) of acquiring and installing the heat pump system. Please be aware that the costs are defined in EUR/kW_th(out) | Link to additional information / German translation
|  |  | Investment costs | EUR | 4500000 |  | The total upfront investment needed for acquiring and installing the heat pump system. | Link to additional information / German translation
|  |  | Other one-time expenses | EUR | 0 |  | Non-recurring costs that arise during the project but are not directly related to equipment or installation (e.g. site preparation, permits and approvals, engineering or administrative fees) excluding planning as these costs are supposed to be provided below. Enter if applicable. | Link to additional information / German translation
|  |  | Total one-time expenses and costs excl. planning costs | EUR | 4500000 |  | The sum of all upfront costs for the heat pump system except planning-related expenses. It combines investment costs and other one-time expenses. | Link to additional information / German translation
|  |  | Regular annual expenses (heat pump specific) | EUR/yr | 0 |  | This parameter includes fixed annual expenses related to the operation of the heat pump system, such as personnel, rent, or service contracts—if applicable. It is considered equivalent to the corresponding value for the heat pump (as referenced in cell >O&M Costs - variable (excl. electricity)<), normalized to the pump's installed capacity (3 MW). | Link to additional information / German translation
|  |  | O&M Costs - fix | EUR/MW_th/yr | 22000 |  | Operation & Maintenance costs that do not depend on system usage. These may include annual inspections, routine maintenance, and service contracts. Has the same impact as the >Regular annual expenses (heat pump specific)< defined above, but is specified per MW_th (nominal capacity) of the heat pump. | Link to additional information / German translation
|  |  | Total operation independent O&M costs related to heat pump: regular annual expenses (heat pump specific) + O&M Costs - fix * nominal capacity of heat pump | EUR/yr | 66000 |  | Refers to the total fixed annual costs needed to keep the heat pump in good working condition, regardless of how much heat it delivers. | Link to additional information / German translation
|  |  | O&M Costs - variable (excl. electricity) | EUR/MWh_th | 0 |  | These are usage-dependent operational costs, excluding electricity. Examples include replacement of parts due to wear, maintenance that varies with operating hours or load, ronsumables (e.g., refrigerant top-up). Enter if relevant. | Link to additional information / German translation
|  |  | Electricity - grid fee and other electrical capacity-related costs | EUR/kW_electr_HP/yr | 150 |  | These are the consumption-independent electricity costs (e.g. grid charge, "LEISTUNGSPREIS" in German) in EUR/kW/yr that come on top of the electricity price (specified in the sheet >Definition of Typical Day<) that need to be paid per yr | Link to additional information / German translation
|  |  | Electricity - grid fee and other electrical capacity-related costs | EUR/yr | 150000 |  | These are the annual consumption-independent electricity (grid) costs ("LEISTUNGSPREIS" in German), calculated by Electricity grid fee (cell above) in EUR/MWh times heat pump capacity (MW) / COP_nominal. This means that the grid fee costs are based on the nominal heat pump performance, not the actual worst case power demand (high temperature, low COP) or the actual rated nominal electricity load capacity of the grid connection.
|  |  | Electricity - grid fee and other electricity consumption-related costs | EUR/MWh_electr_fuel | 11 |  | These are the consumption-dependent electricity costs (e.g. grid charge) that come on top of the electricity price (specified in the sheet >Definition of Typical Day<) that need to be paid when the heat pump system is running. To convert from EURCent/kWh, multiply by 10. | Link to additional information / German translation
Subsidies
|  |  | S1 (one-time, lump sum per MW) | EUR/kW_th | 600 |  | One-time investment grant per unit of installed capacity, e.g. investment funding under the German 'Bundesförderung für effiziente Wärmenetze (BEW)', which covers up to 40% of the eligible capital costs of purchasing and installing the heat pump. Please be aware that the costs are defined in EUR/kW_th(out) | Link to additional information / German translation
|  |  | S1 total lump sum subsidies | EUR | 1800000 |  | Total one-time investment grant for the heat pump system | Link to additional information / German translation
|  |  | S2 (annually) for given number of yrs | EUR/MW_th/yr | 0 |  | This considers annual (operation-independent) subsidies for a defined number of year (10 years, as defined in the section: (>S2 given for number of years<), for which the subsidies are given. If subsidies are given under a Take-or-Pay premise, then use this variable to specifiy the subsidies instead of S3 below. | Link to additional information / German translation
|  |  | S2 given for number of years | Years | 10 |  | Number of years, for which the annual (operation-independent) subsidies S2 (defined above) are given. | Link to additional information / German translation
|  |  | S2 (annually), average for calculatory project lifetime | EUR/MW_th/yr | 0 |  | This considers annual (operation-independent) subsidies for the entire lifetime of project (15 years, as defined in the section Economic settings below). | Link to additional information / German translation
|  |  | S3 (annually, based on supplied waste heat (WH) by DC). PLEASE BE AWARE THAT THIS KIND OF SUBSIDY IS ONLY PROVIDED BY SOME COUNTRIES, E.G. GERMANY | EUR/MWh_th (utilised waste heat, not HP output or electricity input) | 0 | Calculate appropriate value according to German BEW (2026) | This subsidy applies to projects utilizing waste heat, often in combination with heat pumps. It is a subsidy per utilized MWh of Waste heat (provided by DC under Pay-as-you-go contract, NOT the MWh provided to the district heating network or the heat provided by the Heat pump) for a defined lifetime of project (10 years, as defined in the section >S3 given for number of years<). | Link to additional information / German translation
|  |  | S3 given for number of years | Years | 10 |  | Number of years, for which the annual (operation-dependent) subsidies S3 (defined above) are given. | Link to additional information / German translation
|  |  | S3, average for calculatory project lifetime | EUR/MWh_th (utilised waste heat, not HP output or electricity input) | 0 |  | Subsidy for waste heat utilization. Within the calculation it is ensured that subsidies provided do not exceed the sum of electricity costs for running the heat pump and the auxiliary electricity demand. | Link to additional information / German translation
|  |  | Consider subsidies (S3) in dispatch | 1/0 | 0 |  | If 1 is defined, then the average subsidies S3, currently set to 0 EUR/MWh_th are considered in the dispatch. If any other value is provided, then the subsidies are considered in the project evaluation, but not for the dispatch ('EINSATZPLANUNG' of the heat pump). Current Setting: NOT CONSIDERED IN DISPATCH | Link to additional information / German translation
The following heat pump-related subsidies are currently considered: Lump-sum-subsidies: 1800000 EUR (one-time, lump sum) + capacity related subsidies: 0 EUR/MW_th/yr + operation-related subsidies: 0 EUR/MWh_th (utilised waste heat, not HP output or electricity input)
HEAT PUMP AND BOOSTER SYSTEM INCLUDING HEAT EXCHANGER AND PIPING TO THE DH GRID (B2 - B3) | Booster
Technical data
|  |  | Generating capacity | MW_th | 0.5 | Under current settings, a booster capacity of up to 0.19 MW is needed to fully utilise the heat. | Thermal output that defines the maximum amount of heat the booster can deliver. In this tool, the booster is used to raise the temperature of the heat pump’s sink outlet flow when the required temperature level exceeds what the heat pump alone can provide. | Link to additional information / German translation
|  |  | Efficiency | % | 99 |  | The conversion efficiency of the booster technology that indicates how effectively it converts input energy (e.g., electricity or fuel) into usable heat. An additional 1% loss is assumed downstream of the booster, similar to the loss factor applied to the heat pump output. | Link to additional information / German translation
Economic data
|  |  | Specific investment costs | EUR/kW_th | 150 |  | The cost of purchasing and installing the booster system per kilowatt of thermal capacity. Please be aware the costs are defined in EUR/kW_th(out) | Link to additional information / German translation
|  |  | Investment costs | EUR | 75000 |  | The total capital expenditure for the booster, including all equipment and installation costs for the full system (not per unit). | Link to additional information / German translation
|  |  | Other one-time expenses | EUR | 0 |  | Covers all non-recurring project-specific costs, such as site preparation, permitting, and documentation — excluding planning/design costs as they are supposed to be provided below. | Link to additional information / German translation
|  |  | Total one-time expenses and costs excl. Planning costs | EUR | 75000 |  | The sum of all initial expenditures, including investment costs and other one-time expenses, but excluding planning costs. | Link to additional information / German translation
|  |  | Regular annual expenses (booster specific) | EUR/yr | 2000 |  | General recurring costs such as rent, personnel, or administrative fees directly related to the booster system. | Link to additional information / German translation
|  |  | O&M Costs - fix | EUR/MW_th/yr | 0 |  | Fixed annual operation & maintenance costs per MW of installed thermal capacity. May include costs like preventive maintenance, inspections, and service contracts. Enter if applicable. | Link to additional information / German translation
|  |  | Total operation independent O&M costs related to booster | EUR/yr | 2000 |  | The sum of all fixed annual costs associated with the booster system, independent of its usage. | Link to additional information / German translation
|  |  | O&M Costs - Variable | EUR/MWh_th | 0 |  | Variable costs per unit of thermal energy delivered. This includes usage-dependent expenses like consumables, wear-related replacements, and performance-based servicing. | Link to additional information / German translation
|  |  | Electricity / fuel - grid fee and other capacity-related costs | EUR/kW_electr_HP/yr | 150 |  | These are the consumption-independent fuel/electricity costs (e.g. grid charge) that come on top of the electricity/fuel price (specified in the sheet >Definition of Typical Day<) that need to be paid per year | Link to additional information / German translation
|  |  | Electricity - grid fee and other electrical capacity-related costs | EUR/yr | 75757.5758 |  | These are annual consumption-independent electricity (grid) costs ("LEISTUNGSPREIS" in German), calculated by electricity grid fee (cell above) in EUR/MWh for the Booster. This means that the grid fee costs are based on the booster capacity and performance, not the actual rated nominal electricity load capacity of the grid connection.
|  |  | Electricity / fuel - grid fee and other consumption-related costs | EUR/MWh_electr_fuel | 11 |  | These are the consumption-dependent electricity/fuel costs (e.g. grid charge) that come on top of the electricity/fuel price (specified in the sheet >Definition of Typical Day<) that need to be paid when the booster system is running. To convert from EURCent/kWh, multiply by 10. | Link to additional information / German translation
Subsidies for booster operation
|  |  | S1 (one-time, lump sum per MW) | EUR/MW_th | 0 |  | If applicable. A one-time financial support granted per installed megawatt of thermal capacity (MW_th) of the heat pump system. | Link to additional information / German translation
Piping (from DH grid to B2) and heat exchanger (HEx 2)
|  |  | Investment costs in HEx2 (equipment, installation, heat exchangers, one-time, lump-sum) | EUR | 500000 |  | Investment costs excluding planning cost and excluding subsidies (if applicable). Covers the full cost of installing piping and heat exchangers, including materials and labour, as a one-time payment. | Link to additional information / German translation
|  |  | Investment costs for heat network from DH grid to B2 (see >Grid Costs<) | EUR | 1050000 |  | Investment costs excluding planning cost and excluding subsidies (if applicable). Refers to the capital costs for the heat distribution network (e.g., main and branch pipelines, valves). | Link to additional information / German translation
Planning costs
|  |  | Planning costs [% total investment costs: Heat pump, booster, heat network, heat exchanger] | % | 8 |  | Share of the total investment allocated to project planning and engineering (e.g., design, permitting, studies). | Link to additional information / German translation
|  |  | Total Investment costs (HP, booster, heat network, heat exchanger, etc.) | EUR | 6125000 |  | Sum of all relevant upfront investments used as the basis for calculating the planning cost share. | Link to additional information / German translation
|  |  | Planning costs [absolute] | EUR | 490000 |  | Total planning cost calculated from the percentage share above. | Link to additional information / German translation
Other OPEX
|  |  | Auxiliary electricity consumption (share of heat gen.) | % | 2 |  | Proportion of total heat generation requiring auxiliary electricity (e.g., for circulation pumps, control systems). | Link to additional information / German translation
|  |  | Personnel | EUR/yr | 20000 |  | Annual personnel costs associated with system operation (if applicable). | Link to additional information / German translation
|  |  | Rent | EUR/yr | 0 |  | Annual rental costs for land, buildings, or space used by the energy system (if applicable). | Link to additional information / German translation
Other end-of-the-lifetime CAPEX
|  |  | Demolition costs | EUR | 0 |  | Specify the decommission costs, that occur at the end of the project lifetime (20 years, as specified in >Decommissioning after how many years<). Leave empty, if these costs shall not be considered. | Link to additional information / German translation
|  |  | Residual value of investment at the end of the lifetime | EUR | 0 |  | Specify the expected remaining value of the investment at the end of the project lifetime (20 years, as specified in >Decommissioning after how many years<), e.g., resale value or salvaged equipment, if it is to be considered.. | Link to additional information / German translation
Contractor 1 / district heating operator | Economic settings
|  |  | Decommissioning after how many years | Years | 20 |  | Defines the expected technical or economic end-of-life for the infrastructure (default: 20 years). | Link to additional information / German translation
|  |  | Depreciation time of project / calculatory lifetime | Years | 15 |  | Number of years over which the investment is financially depreciated in calculations (default: 15 years). | Link to additional information / German translation
|  |  | Energy carrier price increase on top of inflation | % | 0 |  | Annual increase in fuel or energy carrier prices in real terms, i.e., beyond inflation (default: 0%). | Link to additional information / German translation
Project-specific interest rate
|  | a) Based on weighted average costs of capital (WACC) |  |  |  |  | Alternative a) Calculate WACC
|  |  | Average interest rate of loans in real terms (excluding inflation) | % | 2.5 |  | Effective borrowing cost after adjusting for inflation (default: 2.5%). While banks provide interest rates in nominal terms, economic calculations often require the real interest rate to accurately assess the true cost of capital over time. E.g. a loan is defined as 6M EURIBOR + 1%. If the 6M EURIBOR is at 4%, the inflation rate at 3%, then interest rate in real terms is defined as 4% + 1% - 3% = 2% | Link to additional information / German translation
|  |  | Expected interest rate on equity, again in real terms | % | 7 |  | Return required by equity investors, inflation-excluded (default: 7.0%). Inflation rate is subtracted like above. | Link to additional information / German translation
|  |  | Share of equity capital on total financing | % | 20 |  | Capital structure of the project (default: 20%). | Link to additional information / German translation
|  |  | Corporate tax rate | % | 20 |  | Tax rate used to calculate WACC after tax (default: 20%). | Link to additional information / German translation
|  |  | Weighted average costs of capital (WACC) | % | 3 |  | Weighted average cost of capital, combining debt and equity financing. | Link to additional information / German translation
|  | b) Set expected IRR manually |  |  |  |  | Alternative b) Use company-internal expected IRR for such project.
|  |  | Required (company internal) rate of return for such project | % | 5 |  | If expected IRR defined, then this variable is used instead of WACC. Please be aware, that expected IRR excluding inflation shall be used. | Link to additional information / German translation
Rate of return used in the subsequent calculations
|  |  | Rate of return used in the subsequent calculations | % | 5 |  | Expected IRR used for calculation | Link to additional information / German translation
|  |  | Capital recovery factor (annuity factor) | 1/yr | 0.096342 |  | Factor used to annualize capital costs based on interest rate and lifetime | Link to additional information / German translation
WASTE HEAT RECOVERY SYSTEM FROM DATA CENTRE: B1 - B2 | Investments and running costs | [7 empty] | CONTRACTOR 2 / DC OPERATOR
|  | Economic Data |  |  |  | Share paid by Contractor 1
|  |  | Investment costs (equipment, installation, heat exchangers, one-time, lump sum) | EUR | 500000 | 0% | Investment costs excluding planning cost and excluding subsidies (if applicable). Covers the full cost of installing piping and heat exchangers, including materials and labour, as a one-time payment. | Link to additional information / German translation
|  |  | Investment costs for heat network (see >Grid Costs<) | EUR | 126000 | 0% | The investment costs for the necessary heat network, can be defined in the sheet Grid Costs | Link to additional information / German translation
|  |  | Total one-time expenses and costs excl. Planning costs | EUR | 626000 |  | Total investment allocated to project planning and engineering (e.g., design, permitting, studies). | Link to additional information / German translation
|  |  | Planning costs [% Investment costs] | % | 8 |  | Share of >Total one-time expenses and costs excl. Planning costs< | Link to additional information / German translation
|  |  | Planning costs [absolute] | EUR | 50080 | 0% | Total planning cost calculated from the percentage share above. | Link to additional information / German translation
|  |  | Regular annual expenses (WASTE HEAT RECOVERY specific) | EUR/yr | 50000 | 0% | General recurring costs such as rent, personnel, or administrative fees directly related to the heat recovery. | Link to additional information / German translation
|  |  | O&M Costs - Variable (incl. electricity) | EUR/MWh_th | 2 | 0% | Variable costs per unit of thermal energy delivered by data centre. Has the same impact as the >Regular annual expenses (waste heat recovery specific)< defined above, but is specified per MWh_th. | Link to additional information / German translation
|  |  | Heat price (Take-or-Pay) p_0 | EUR/MWh_th | 0 | 0% | Price p_0 is the payment for waste heat from the data Centre to an external third party. This price and associated costs are not considered as revenues for either Contractor 1 or Contractor 2 / DC operator but are revenues for a third party not within the scope of this tool. Note that these are to be considered costs that occur before considering the necessary investments by the Contractor 2 / DC operator. If a price is defined, then it is considered under Take-or-Pay conditions. | Link to additional information / German translation
|  | Subsidies |  |  | Share received by Contractor 1
|  |  | S1 (one-time, lump sum) | EUR | 0 | 0 | One-time investment grant; if applicable | Link to additional information / German translation
Contractor 2 / data centre operator | Economic setting
|  |  | Depreciation time of project / Calculatory lifetime | Years | 15 |  |  | Link to additional information / German translation
Project-specific interest rate
|  | a) Based on weighted average costs of capital (WACC) |  |  |  |  | Alternative a) Calculate WACC
|  |  | Average interest rate of loans in real terms (excluding inflation) | % | 2.5 |  | Effective borrowing cost after adjusting for inflation (default: 2.5%). While banks provide interest rates in nominal terms, economic calculations often require the real interest rate to accurately assess the true cost of capital over time. E.g. a loan is defined as 6M EURIBOR + 1%. If the 6M EURIBOR is at 4%, the inflation rate at 3%, then interest rate in real terms is defined as 4% + 1% - 3% = 2% | Link to additional information / German translation
|  |  | Expected interest rate on equity, again in real terms | % | 7 |  | Return required by equity investors, inflation-excluded (default: 7.0%). Inflation rate is subtracted like above. | Link to additional information / German translation
|  |  | Share of equity capital on total financing | % | 20 |  | Capital structure of the project (default: 20%). | Link to additional information / German translation
|  |  | Corporate tax rate | % | 20 |  | Tax rate used to calculate WACC after tax (default: 20%). | Link to additional information / German translation
|  |  | Weighted average costs of capital (WACC) | % | 3 |  | Weighted average cost of capital, combining debt and equity financing. | Link to additional information / German translation
|  | b) Set expected IRR manually |  |  |  |  | Alternative b) Use company-internal expected IRR for such project.
|  |  | Required (company internal) rate of return for such project | % | 5 |  | If expected IRR is defined, then this variable is used instead of WACC. If empty, than the WACC calculated above is used. Please be aware, that IRR excluding inflation shall be used. | Link to additional information / German translation
Rate of return used in the subsequent calculations
|  |  | Rate of return used in the subsequent calculations | % | 5 |  | Rate of return used for calculation | Link to additional information / German translation
|  |  | Capital recovery factor (annuity factor) | 1/yr | 0.096342 |  | Factor used to annualize capital costs based on interest rate and lifetime | Link to additional information / German translation
Default active cooling system
|  |  | Average weighted annual SCOP of active cooling unit |  | 7.5 |  | This is the average achieved ratio of removed thermal energy-to-electricity, weighted considering different operation conditions. Only for those hours, where active cooling is running and not considering the periods, where free cooling is applied. The ratio between active cooling and free cooling as well as the electricity price is defined in the sheet >Definition of Typical Day<.
|  |  | Electricity - grid fee | EUR/MWh_electr | 11 |  | These are the consumption-dependent electricity costs that come on top of the electricity price (specified in the sheet >Definition of Typical Day<) that need to be paid when the active cooling system is running. We do not consider additional capacity-related grid costs. To convert from EURCent/kWh, multiply by 10. | Link to additional information / German translation
Check COP at alternative temperature levels based on settings for S - Source, S - Flow and S - Return
|  |  | Alternative heat source in temperature (e.g. DC waste heat temperature) | 30 | Alternative temperature COP (30°C instead of 25°C) | 3.1
|  |  | Alternative heat sink out temperature (e.g. district heat supply line temperature) | 80 | Alternative temperature COP (80°C instead of 90°C) | 3.26
|  |  | Alternative heat sink in temperature (e.g. district heat return line temperature) | 45 | Alternative temperature COP (45°C instead of 60°C) | 3
|  |  | Combined effect: Alternative temperature COP (30°C instead of 25°C), (80°C instead of 90°C), (45°C instead of 60°C) |  |  | 3.36
S - Source, S - Flow and S - Return values as defined above
|  |  | S - Source | 0.02 |  | Go to settings above
|  |  | S - Flow | 0.026 |  | Go to settings above
|  |  | S - Return | 0 |  | Go to settings above
Calculated subsidies based on "Bundesförderung für effiziente Wärmenetze (BEW)", Merkblatt Antragstellung, technische Anforderungen und Verwendungsnachweis, v3, 01.01.2026
|  |  | This is relevant under German law (BEW) only and thus partly in German |  |  |  |  | https://www.bafa.de/SharedDocs/Downloads/DE/Energie/bew_merkblatt_20251216.pdf
|  |  | SCOP, as currently calculated for the project based on this tool (HP_heat_output_per_year /HP_electricity_input_per_year) | - | 3.4438
|  |  | SCOP | - | 3.47 | Dieser Wert muss manuell eingegeben werden | Use appropriate annual SCOP value
Wärmepumpen mit allgemeiner Versorgung (§3 Nr. 17EnWG)
|  |  | Förderbetrag | Cent/kWh | 5.7239 |  | As according to formula to the right
|  |  | Fördersumme je 1 kWh Strominput | Cent/kWh_Strom | 14.138 |  | As according to formula to the right
|  |  | Fördersumme je 1 kWh Abwärme | Cent/kWh_Abwärme | 5.7239
|  |  | Fördersumme je 1 MWh Abwärme | EUR/MWh_Abwärme | 57.2389 | Dies ist der Wert, der oben manuell (S3) einzusetzen ist; es gibt keine automatische Verknüpfung! | Go to settings above
Wärmepumpen mit Strom aus EE-Erzeugern ohne Durchleitung öffentliches Netz
|  |  | Förderbetrag | Cent/kWh | 2.3291 |  | As according to formula to the right
|  |  | Fördersumme je 1 kWh Strominput | Cent/kWh_Strom | 8.082 |  | As according to formula to the right
|  |  | Fördersumme je 1 kWh Abwärme | Cent/kWh_Abwärme | 3.2721
|  |  | Fördersumme je 1 MWh Abwärme | EUR/MWh_Abwärme | 32.7206 | Dies ist der Wert, der oben manuell (S3) einzusetzen ist; es gibt keine automatische Verknüpfung! | Go to settings above
Eine Betriebskostenförderung kann nicht gewährt werden, wenn die Wärmepumpe direkt mit eigens produziertem fossilem Strom betrieben wird. In Ausnahmefällen kann eine bilanzielle Trennung der Strommengen genehmigt werden, wenn es stromnetzseitig nicht möglich ist, die Wärmepumpe und den fossilen Stromerzeuger voneinander zu trennen.
Für Wärmepumpen, die den Strom aus dem Netz der allgemeinen Versorgung (§3 Nr. 17 EnWG) oder aus einem geschlossenen Verteilnetz (§110 EnWG) beziehen, gilt folgende Formel zur Berechnung des Förderbetrags:
Förderbetrag = [5,5 − (6,8 − 17 / (SCOP bzw. JAZ)) * 0,75] * (SCOP bzw. JAZ / (SCOP bzw. JAZ − 1)) Cent/kWh
Der Förderbetrag ist auf 9,2 Cent/kWh netto begrenzt. Die Fördersumme berechnet sich dann mit der Formel:
Fördersumme = (Strommenge * SCOP bzw. JAZ − Strommenge) * Förderbetrag
Die Strommenge wird subtrahiert, da kein Strom aus fossiler Energie gefördert werden soll. Zusätzlich gilt eine Begrenzung auf 90% nachgewiesenen Stromkosten. D. h. die vom Antragsteller angegebenen Stromkosten werden mit 90% multipliziert und diese Summe mit der berechneten Fördersumme aus Strombezug und dem Förderbetrag in Cent/kWh sowie der Summer aus der WLB verglichen. Die niedrigste Summe entspricht dann der Förderung. Im VN werden ebenfalls nur 90% der Stromkosten berücksichtigt.
Bezieht eine Wärmepumpe Strom aus EE-Erzeugern ohne dass der Strom durch das öffentliche Stromnetz geleitet wird und kann durch ein entsprechendes Messkonzept der Bezug der Wärmepumpe von den EE-Erzeugern eindeutig erfasst werden gilt folgende Formel zur Berechnung der Förderung:
Förderbetrag = 3 − (8 / (2,5 × SCOP bzw. JAZ)) × 0,75 Cent/kWh
Der Förderbetrag ist auf 3 Cent/kWh netto begrenzt. Die Fördersumme berechnet sich dann mit der Formel:
Fördersumme = Strombezug (aus der erneuerbaren Energiequelle) × SCOP bzw. JAZ × Förderbetrag
Wer der Eigentümer der EE-Erzeuger ist, ist dabei nicht relevant. Biogas-KWK werden als EE-Stromerzeuger akzeptiert.
Um entgangene Einnahmen EE geltend zu machen muss der Antragsteller folgendes liefern:
Fördersatz mit Angabe einer offiziellen Quelle der Fördersätze.
Berechnung, wie sich die entgangene Förderung ergibt.
Formlose Erklärung/Bestätigung, dass die Anlage eine Förderung erhalten würde.
Aufstellung der erzeugten Strommenge und des Verbrauchs der Wärmepumpe pro Monat.
Wird Strom aus beiden Varianten bezogen, muss ein entsprechendes Messkonzept die Anteile am Strom der beiden Varianten aufzeigen. Ist dies nicht möglich und befinden sich EE-Erzeuger und nicht EE-Erzeuger im selben Strom-/Verteilnetz kann so abgerechnet werden, als würde die Wärmepumpe zu 100% mit Strom aus dem öffentlichen Netz betrieben werden.
Wird eine förderfähige Wärmepumpe mit einer KWK-Anlage betrieben, kann eine Betriebskostenförderung gewährt und der überschüssige Strom darf verkauft werden, wenn dieser keine andere Vergütung erhält. Der Förderbetrag entspricht dann dem Förderbetrag, wie wenn die Wärmepumpe Strom aus dem Netz der öffentlichen Versorgung bezieht.
Als Nachweis für die tatsächlichen Kosten bei Stromnetzbezug ist die Rechnung des Stromanbieters und Bilder von den Wärme- und Strommengenzählern einzureichen, die sich auf die Strommengen der Wärmepumpen bezieht.
Wirtschaftlichkeitslückenberechnung
Als Investitionskosten dürfen nur die Kosten für die Komponenten angegeben werden, die im (S)COP bzw. der JAZ berücksichtigt wurden. Daneben können die Kosten für die Komponenten zur Förderung des Wärmemediums sowie die Stromanlagen und Steuerungstechnik berücksichtigt werden, die unmittelbar für deren Betrieb notwendig sind. Zum Nachweis der Kosten ist dem Antrag eine Aufstellung der im Modul 2 als förderfähig anerkannten Kosten beizufügen. Zu jeder Kostenposition ist auf denselben Nachweis wie im Modul 2 zu referenzieren und dieser Nachweis beizufügen. Sollten sich Änderungen zum Antrag Modul 2 ergeben haben, ist dies kenntlich zu machen und die aktuellen Dokumente beizufügen.

## Grid Costs
Go to Content
Colour Code | Header
Item / unit
User input
Cell with formula
Go to Content
Input - not used for calculation
Control cells
Contractor 1 (district heating operator)
| Dimension (DN) | mm | 20 | 25 | 32 | 40 | 50 | 65 | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000
Link to additional information / German translation | Specific cost (including pipe works and joints) | EUR/m | 760 | 800 | 856 | 920 | 1000 | 1120 | 1240 | 1400 | 1600 | 1800 | 2200 | 2600 | 3000 | 3400 | 3800 | 4200 | 4600 | 5400 | 6200 | 7000 | 7800 | 8600
| Trench / pipe length per DN (Ensure that consistent use of either trench or pipe length is used) | [23 empty] | Totals
| Pipe length existing DH network (B3) to heat exchanger 2 (HEx 2), if applicable | m | [15 empty] | 200 | [6 empty] | Pipe length from HP to Booster | EUR | 840000
| Pipe length heat exchanger 2 to heat pump including piping needed to connect booster (if applicable) | m | [15 empty] | 20 | [6 empty] | Pipe length from HP to DH grid | EUR | 84000
| Pipe length from heat pump to system boundary B2 | m | [15 empty] | 30 | [6 empty] | Pipe length from Booster to DH grid | EUR | 126000
| Total pipe length within system boundary: Contractor 1 | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | Total pipe length within system boundary: Contractor 1 | EUR | 1050000
| Investment costs for network invested by Contractor 1 | EUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050000 | 0 | 0 | 0 | 0 | 0 | 0 | Total investment | EUR | 1050000
Contractor 2 (data centre operator)
| Dimension (DN) | mm | 20 | 25 | 32 | 40 | 50 | 65 | 80 | 100 | 125 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 700 | 800 | 900 | 1000
| Specific cost (including pipe works and joints) | EUR/m | 760 | 800 | 856 | 920 | 1000 | 1120 | 1240 | 1400 | 1600 | 1800 | 2200 | 2600 | 3000 | 3400 | 3800 | 4200 | 4600 | 5400 | 6200 | 7000 | 7800 | 8600
| Trench / pipe length per DN (Ensure consistent use of either trench or pipe length) | [23 empty] | Totals
| Total pipe length from within system boundary B2 to system boundary B1 (existing waste heat source): Contrator 2 / data centre operator | m | [15 empty] | 30 | [6 empty] | Pipe length from data centre to HP | EUR | 126000
| Investment costs for network invested by Contrator 2 / data centrer operator | EUR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126000 | 0 | 0 | 0 | 0 | 0 | 0 | Total investment | EUR | 126000
Contractor 1 (district heating operator)
Contractor 2 (data centre operator)
Note: Figures reflect each contractor's own data and are not mutually aligned.

## Definition of Typical Day
Go to Content
Header | Colour Code
Item / unit
User input
Cell with formula
Go to content
Input - not used for calculation
Control cells |  | Define meaningful "typical days" for the desired project and your demands
Check settings / input data, there might be some error
| Typical day |  | Typical day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Link to additional information / German translation |  | Name of typical day | Name of typical day | Winter day | Spring / fall weekday | Spring / fall weekend | Summer weekday | Summer weekend | Maintenance of HP | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Link to additional information / German translation |  | Season of typical day | Season of typical day | Winter | Spring / Fall | Spring / Fall | Summer | Summer | Can occur in any season | [14 empty] | Season
Link to additional information / German translation |  | Qualitative Description |  | The amount of waste heat is significantly lower than the heat demand. The grid supply temperature is higher than the maximum heat pump temperature, so additional heating via direct electric heating is required. | On a typical fall weekday, the amount of waste heat is clearly lower than the demand in the existing network. Supply temperatures are not very high yet. | Similar to the weekday scenario – on a fall weekend, the amount of waste heat remains lower than demand, and supply temperatures are still not very high. | On a summer weekday, the supply temperature is lower, and all the available waste heat can be used. | Same as on the weekday – lower supply temperatures allow full utilization of the available waste heat. | The heat pump is out of operation either due to maintenance or due to no heat demand. | [14 empty] | Qualitative Description
|  |  | Outside Temperature | [20 empty] | Outside Temperature
|  |  | Available waste heat | High | Moderate | Moderate | [17 empty] | Available waste heat
|  |  | Waste heat higher than demand | No | No | No | [17 empty] | Waste heat higher than demand
|  |  | Waste heat temperature | Constant | Constant | Constant | Constant | Constant | [15 empty] | Waste heat temperature
|  |  | Grid temperature | High | Medium | Medium | Low | Low | [15 empty] | Grid temperature
0
|  |  | HP outage / maintenance | No | No | No | No | No | Yes | [14 empty] | HP outage / maintenance
|  | Economic parameters | [21 empty] | Economic parameters
0
Link to additional information / German translation |  | Electricity price auxiliary electricity (for simplicity, this price includes already grid fees, etc.). | EUR/MWh | 135 | 71 | 71 | 60 | 60 | 66 | [14 empty] | Electricity price auxiliary electricity (for simplicity, this price includes already grid fees, etc.).
Technical parameters
|  | Filter for Variable | Filter for hour of the day
| 1 | Available waste heat (DC heat source) | Hour of day | Available waste heat (DC heat source) | [19 empty] | Hour of the day
Link to additional information / German translation | 1 | Available waste heat (DC heat source) |  | MW_th
| 1 | Available waste heat (DC heat source) |  | Hourly thermal output from the data centre that is available for heat recovery. This represents the maximum potential heat input for the heat pump system. In order to consider a scheduled maintenance of the heat pump, the available waste heat can be set to Zero if there is no need to renumerate the waste heat provided by the DC/waste heat operator (e.g in a pay-as-you-go contract)
| 1 | Available waste heat (DC heat source) | 1 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 1
| 1 | Available waste heat (DC heat source) | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 2
| 1 | Available waste heat (DC heat source) | 3 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 3
| 1 | Available waste heat (DC heat source) | 4 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 4
| 1 | Available waste heat (DC heat source) | 5 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 5
| 1 | Available waste heat (DC heat source) | 6 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 6
| 1 | Available waste heat (DC heat source) | 7 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 7
| 1 | Available waste heat (DC heat source) | 8 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 8
| 1 | Available waste heat (DC heat source) | 9 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 9
| 1 | Available waste heat (DC heat source) | 10 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 10
| 1 | Available waste heat (DC heat source) | 11 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 11
| 1 | Available waste heat (DC heat source) | 12 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 12
| 1 | Available waste heat (DC heat source) | 13 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 13
| 1 | Available waste heat (DC heat source) | 14 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 14
| 1 | Available waste heat (DC heat source) | 15 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 15
| 1 | Available waste heat (DC heat source) | 16 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 16
| 1 | Available waste heat (DC heat source) | 17 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 17
| 1 | Available waste heat (DC heat source) | 18 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 18
| 1 | Available waste heat (DC heat source) | 19 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 19
| 1 | Available waste heat (DC heat source) | 20 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 20
| 1 | Available waste heat (DC heat source) | 21 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 21
| 1 | Available waste heat (DC heat source) | 22 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 22
| 1 | Available waste heat (DC heat source) | 23 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 23
| 1 | Available waste heat (DC heat source) | 24 | 2 | 2 | 2 | 2 | 2 | 0 | 20 20: 0.001 | 24
| 1 |  | Daily average | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | Daily average
1
Link to additional information / German translation | 2 | Max heat demand - grid (HP heat sink) | Hour of day | Max heat demand - grid (HP heat sink) | [19 empty] | Hour of day
| 2 | Max heat demand - grid (HP heat sink) |  | MW_th
| 2 | Max heat demand - grid (HP heat sink) |  | Hourly thermal demand from the district heating network that the heat pump can supply. It sets the upper limit for how much heat can be delivered into the grid. In order to consider a scheduled maintenance of the heat pump, the grid demand can be set to Zero (if the entire system shall not run) but the DC / waste heat operator provides heat and is supposed to be renumerated for that heat in a take-or-pay contract
| 2 | Max heat demand - grid (HP heat sink) | 1 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 1
| 2 | Max heat demand - grid (HP heat sink) | 2 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 2
| 2 | Max heat demand - grid (HP heat sink) | 3 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 3
| 2 | Max heat demand - grid (HP heat sink) | 4 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 4
| 2 | Max heat demand - grid (HP heat sink) | 5 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 5
| 2 | Max heat demand - grid (HP heat sink) | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 6
| 2 | Max heat demand - grid (HP heat sink) | 7 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 7
| 2 | Max heat demand - grid (HP heat sink) | 8 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 8
| 2 | Max heat demand - grid (HP heat sink) | 9 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 9
| 2 | Max heat demand - grid (HP heat sink) | 10 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 10
| 2 | Max heat demand - grid (HP heat sink) | 11 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 11
| 2 | Max heat demand - grid (HP heat sink) | 12 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 12
| 2 | Max heat demand - grid (HP heat sink) | 13 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 13
| 2 | Max heat demand - grid (HP heat sink) | 14 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 14
| 2 | Max heat demand - grid (HP heat sink) | 15 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 15
| 2 | Max heat demand - grid (HP heat sink) | 16 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 16
| 2 | Max heat demand - grid (HP heat sink) | 17 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 17
| 2 | Max heat demand - grid (HP heat sink) | 18 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 18
| 2 | Max heat demand - grid (HP heat sink) | 19 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 19
| 2 | Max heat demand - grid (HP heat sink) | 20 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 20
| 2 | Max heat demand - grid (HP heat sink) | 21 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 21
| 2 | Max heat demand - grid (HP heat sink) | 22 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 22
| 2 | Max heat demand - grid (HP heat sink) | 23 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 23
| 2 | Max heat demand - grid (HP heat sink) | 24 | 6 | 6 | 6 | 6 | 6 | 0 | 20 20: 100 | 24
| 2 |  | Daily average | 6 | 6 | 6 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | Daily average
Link to additional information / German translation | 2 | Heat source temperature (DC) / temperature of the cooling system before HEx 1
| 3 |  | Hour of day | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | [19 empty] | Hour of day
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 |  | °C
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 |  | Temperature of the waste heat source, after the temperature reduction in the HEx 1 this is the temperature that is entering the heat pump. This influences the efficiency of the heat pump.
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 1 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 1
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 2 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 2
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 3 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 3
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 4 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 4
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 5 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 5
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 6 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 6
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 7 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 7
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 8
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 9 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 9
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 10 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 10
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 11 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 11
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 12 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 12
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 13 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 13
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 14 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 14
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 15 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 15
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 16
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 17 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 17
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 18 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 18
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 19 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 19
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 20
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 21 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 21
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 22 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 22
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 23 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 23
| 3 | Heat source temperature (DC) / temperature of the cooling system before HEx 1 | 24 | 40 | 40 | 40 | 40 | 40 | 40 | 20 20: 30 | 24
| 3 |  | Daily average | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | Daily average
3
Link to additional information / German translation | 4 | DH supply line temperature* | Hour of day | DH supply line temperature* | [19 empty] | Hour of day
| 4 | DH supply line temperature* |  | °C
| 4 | DH supply line temperature* |  | This is the required supply temperature (in °C) that must be delivered to the district heating (DH) network
| 4 | DH supply line temperature* | 1 | 77 | 86.6667 | 86.6667 | 60 | 60 | 73.3333 | 20 20: 93 | 1
| 4 | DH supply line temperature* | 2 | 77 | 86.6667 | 86.6667 | 60 | 60 | 73.3333 | 20 20: 86.6667 | 2
| 4 | DH supply line temperature* | 3 | 77 | 86.6667 | 86.6667 | 60 | 60 | 73.3333 | 20 20: 86.6667 | 3
| 4 | DH supply line temperature* | 4 | 79 | 88.3333 | 88.3333 | 60 | 60 | 74.1667 | 20 20: 88.3333 | 4
| 4 | DH supply line temperature* | 5 | 83 | 90 | 90 | 60 | 60 | 75 | 20 20: 88 | 5
| 4 | DH supply line temperature* | 6 | 93 | 88.3333 | 88.3333 | 60 | 60 | 74.1667 | 20 20: 88.3333 | 6
| 4 | DH supply line temperature* | 7 | 95 | 88.3333 | 88.3333 | 60 | 60 | 74.1667 | 20 20: 88.3333 | 7
| 4 | DH supply line temperature* | 8 | 95 | 86.6667 | 86.6667 | 60 | 60 | 73.3333 | 20 20: 86.6667 | 8
| 4 | DH supply line temperature* | 9 | 93 | 85 | 85 | 60 | 60 | 72.5 | 20 20: 85 | 9
| 4 | DH supply line temperature* | 10 | 92 | 83.3333 | 83.3333 | 60 | 60 | 71.6667 | 20 20: 83.3333 | 10
| 4 | DH supply line temperature* | 11 | 88 | 81.6667 | 81.6667 | 60 | 60 | 70.8333 | 20 20: 81.6667 | 11
| 4 | DH supply line temperature* | 12 | 80 | 80 | 80 | 60 | 60 | 70 | 20 20: 80 | 12
| 4 | DH supply line temperature* | 13 | 78.3333 | 78.3333 | 78.3333 | 60 | 60 | 69.1667 | 20 20: 78.3333 | 13
| 4 | DH supply line temperature* | 14 | 76.6667 | 76.6667 | 76.6667 | 60 | 60 | 68.3333 | 20 20: 76.6667 | 14
| 4 | DH supply line temperature* | 15 | 76.6667 | 76.6667 | 76.6667 | 60 | 60 | 68.3333 | 20 20: 76.6667 | 15
| 4 | DH supply line temperature* | 16 | 75 | 75 | 75 | 60 | 60 | 67.5 | 20 20: 75 | 16
| 4 | DH supply line temperature* | 17 | 76.6667 | 76.6667 | 76.6667 | 60 | 60 | 68.3333 | 20 20: 76.6667 | 17
| 4 | DH supply line temperature* | 18 | 80 | 78.3333 | 78.3333 | 60 | 60 | 69.1667 | 20 20: 78.3333 | 18
| 4 | DH supply line temperature* | 19 | 82 | 80 | 80 | 60 | 60 | 70 | 20 20: 80 | 19
| 4 | DH supply line temperature* | 20 | 83 | 81.6667 | 81.6667 | 60 | 60 | 70.8333 | 20 20: 81.6667 | 20
| 4 | DH supply line temperature* | 21 | 84 | 83.3333 | 83.3333 | 60 | 60 | 71.6667 | 20 20: 83.3333 | 21
| 4 | DH supply line temperature* | 22 | 80 | 85 | 85 | 60 | 60 | 72.5 | 20 20: 85 | 22
| 4 | DH supply line temperature* | 23 | 79 | 85 | 85 | 60 | 60 | 72.5 | 20 20: 85 | 23
| 4 | DH supply line temperature* | 24 | 78 | 86.6667 | 86.6667 | 60 | 60 | 73.3333 | 20 20: 86.6667 | 24
| 4 |  | Daily average | 82.4306 | 83.125 | 83.125 | 60 | 60 | 71.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3056 | Daily average
4
Link to additional information / German translation | 5 | DH return line temperature* | Hour of day | DH return line temperature* | [19 empty] | Hour of day
| 5 | DH return line temperature* |  | °C
| 5 | DH return line temperature* |  | Temperature (in °C) of the water returning from the district heating network to the heat pump.
| 5 | DH return line temperature* | 1 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 1
| 5 | DH return line temperature* | 2 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 2
| 5 | DH return line temperature* | 3 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 3
| 5 | DH return line temperature* | 4 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 4
| 5 | DH return line temperature* | 5 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 5
| 5 | DH return line temperature* | 6 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 6
| 5 | DH return line temperature* | 7 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 7
| 5 | DH return line temperature* | 8 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 8
| 5 | DH return line temperature* | 9 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 9
| 5 | DH return line temperature* | 10 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 10
| 5 | DH return line temperature* | 11 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 11
| 5 | DH return line temperature* | 12 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 12
| 5 | DH return line temperature* | 13 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 13
| 5 | DH return line temperature* | 14 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 14
| 5 | DH return line temperature* | 15 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 15
| 5 | DH return line temperature* | 16 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 16
| 5 | DH return line temperature* | 17 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 17
| 5 | DH return line temperature* | 18 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 18
| 5 | DH return line temperature* | 19 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 19
| 5 | DH return line temperature* | 20 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 20
| 5 | DH return line temperature* | 21 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 21
| 5 | DH return line temperature* | 22 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 22
| 5 | DH return line temperature* | 23 | 45 | 45 | 45 | 45 | 45 | 45 | 20 20: 45 | 23
| 5 | DH return line temperature* | 24 | 45 | 45 | 45 | 45 | 45 | 45 | [14 empty] | 24
| 5 |  | Daily average | 45 | 45 | 45 | 45 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.125 | Daily average
5
Link to additional information / German translation | 6 | Short-run marginal costs of alternative heat production | Hour of day | Short-run marginal costs of alternative heat production | [19 empty] | Hour of day
| 6 | Short-run marginal costs of alternative heat production |  | EUR/MWh_delivered
| 6 | Short-run marginal costs of alternative heat production |  | The cost of producing 1 MWh of heat using alternative sources that the recovered data centre heat replaces. It helps assess the economic competitiveness of using waste heat.
| 6 | Short-run marginal costs of alternative heat production | 1 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 1
| 6 | Short-run marginal costs of alternative heat production | 2 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 2
| 6 | Short-run marginal costs of alternative heat production | 3 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 3
| 6 | Short-run marginal costs of alternative heat production | 4 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 4
| 6 | Short-run marginal costs of alternative heat production | 5 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 5
| 6 | Short-run marginal costs of alternative heat production | 6 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 6
| 6 | Short-run marginal costs of alternative heat production | 7 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 7
| 6 | Short-run marginal costs of alternative heat production | 8 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 8
| 6 | Short-run marginal costs of alternative heat production | 9 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 9
| 6 | Short-run marginal costs of alternative heat production | 10 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 10
| 6 | Short-run marginal costs of alternative heat production | 11 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 11
| 6 | Short-run marginal costs of alternative heat production | 12 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 12
| 6 | Short-run marginal costs of alternative heat production | 13 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 13
| 6 | Short-run marginal costs of alternative heat production | 14 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 14
| 6 | Short-run marginal costs of alternative heat production | 15 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 15
| 6 | Short-run marginal costs of alternative heat production | 16 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 16
| 6 | Short-run marginal costs of alternative heat production | 17 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 17
| 6 | Short-run marginal costs of alternative heat production | 18 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 18
| 6 | Short-run marginal costs of alternative heat production | 19 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 19
| 6 | Short-run marginal costs of alternative heat production | 20 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 20
| 6 | Short-run marginal costs of alternative heat production | 21 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 21
| 6 | Short-run marginal costs of alternative heat production | 22 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 22
| 6 | Short-run marginal costs of alternative heat production | 23 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 23
| 6 | Short-run marginal costs of alternative heat production | 24 | 65 | 60 | 60 | 40 | 55 | 55 | 20 20: 65 | 24
| 6 |  | Daily average | 65 | 60 | 60 | 40 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | Daily average
6
Link to additional information / German translation | 7 | Electricity price heat pump | Hour of day | Electricity price heat pump | [19 empty] | Hour of day
| 7 | Electricity price heat pump |  | EUR/MWh_elec
| 7 | Electricity price heat pump |  | Hourly electricity price paid for operating the heat pump. This directly affects the operating cost and economic feasibility. Be aware that grid fees (per kW and MWh) can be set in the sheet >Project Setting<. Ensure that the prices and fees are not double counted (e.g grid fees is set in Sheet >Project Setting< AND is included here in the energy price, or the other way round is included in neither cells.
| 7 | Electricity price heat pump | 1 | 66 | 71 | 81.85 | 90.11 | 90.49 | 85.98 | 20 20: 66 | 1
| 7 | Electricity price heat pump | 2 | 63.45 | 70.7 | 70.59 | 80.45 | 79.25 | 75.52 | 20 20: 63.45 | 2
| 7 | Electricity price heat pump | 3 | 63.54 | 70.46 | 69.53 | 79.91 | 71.24 | 74.72 | 20 20: 63.54 | 3
| 7 | Electricity price heat pump | 4 | 61.82 | 69.74 | 64.4 | 79.29 | 70.67 | 71.845 | 20 20: 61.82 | 4
| 7 | Electricity price heat pump | 5 | 61.85 | 70.46 | 63.88 | 83.38 | 66.94 | 73.63 | 20 20: 61.85 | 5
| 7 | Electricity price heat pump | 6 | 61.75 | 73.91 | 63.62 | 91.38 | 62.09 | 77.5 | 20 20: 61.75 | 6
| 7 | Electricity price heat pump | 7 | 62.59 | 83.98 | 64.43 | 115.6 | 57.9 | 90.015 | 20 20: 62.59 | 7
| 7 | Electricity price heat pump | 8 | 66.9 | 106.64 | 60.53 | 110.72 | 46.35 | 85.625 | 20 20: 66.9 | 8
| 7 | Electricity price heat pump | 9 | 74.82 | 108.7 | 60.88 | 98.4 | 19.77 | 79.64 | 20 20: 74.82 | 9
| 7 | Electricity price heat pump | 10 | 77.9 | 87.21 | 55.38 | 81.43 | 4.24 | 68.405 | 20 20: 77.9 | 10
| 7 | Electricity price heat pump | 11 | 71.8 | 75.92 | 32.99 | 70 | 0 | 51.495 | 20 20: 71.8 | 11
| 7 | Electricity price heat pump | 12 | 70.77 | 72.02 | 36.96 | 58.75 | -0.05 | 47.855 | 20 20: 70.77 | 12
| 7 | Electricity price heat pump | 13 | 67.73 | 69.35 | 6.06 | 44.34 | -0.1 | 25.2 | 20 20: 67.73 | 13
| 7 | Electricity price heat pump | 14 | 68.78 | 69.29 | 0.28 | 36.5 | -1.05 | 18.39 | 20 20: 68.78 | 14
| 7 | Electricity price heat pump | 15 | 73.39 | 70.64 | -0.9 | 36.2 | -2.21 | 17.65 | 20 20: 73.39 | 15
| 7 | Electricity price heat pump | 16 | 79.11 | 72.26 | 0.75 | 42.54 | -2.05 | 21.645 | 20 20: 79.11 | 16
| 7 | Electricity price heat pump | 17 | 87.8 | 81.06 | 6.01 | 63.79 | -0.27 | 34.9 | 20 20: 87.8 | 17
| 7 | Electricity price heat pump | 18 | 94.93 | 100 | 58.22 | 77.34 | 22.61 | 67.78 | 20 20: 94.93 | 18
| 7 | Electricity price heat pump | 19 | 99.87 | 119.58 | 74.6 | 91.61 | 71.12 | 83.105 | 20 20: 99.87 | 19
| 7 | Electricity price heat pump | 20 | 91.57 | 119.25 | 89.36 | 121.02 | 99.5 | 105.19 | 20 20: 91.57 | 20
| 7 | Electricity price heat pump | 21 | 81.97 | 93.4 | 95.26 | 190.46 | 115.14 | 142.86 | 20 20: 81.97 | 21
| 7 | Electricity price heat pump | 22 | 75.74 | 80.15 | 91.07 | 120 | 115.44 | 105.535 | 20 20: 75.74 | 22
| 7 | Electricity price heat pump | 23 | 74.68 | 77.98 | 89.41 | 106.86 | 114.33 | 98.135 | 20 20: 74.68 | 23
| 7 | Electricity price heat pump | 24 | 69.13 | 74.34 | 88.46 | 91.55 | 99.79 | 90.005 | 20 20: 69.13 | 24
| 7 |  | Daily average | 73.6621 | 82.835 | 55.1508 | 85.9012 | 50.0475 | 70.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6621 | Daily average
7
Link to additional information / German translation | 8 | Energy price for energy used by booster | Hour of day | Energy price for energy used by booster | [19 empty] | Hour of day
| 8 | Energy price for energy used by booster |  | EUR/MWh_fuel
| 8 | Energy price for energy used by booster |  | Energy price for energy carrier used by booster. This might be e.g. electricity (with variable price as it is the case for the electricity used by the heat pump) or gas with with a rather flat profile. Ensure that the efficiency defined in the Project Sheet is set accordingly. Be aware that grid fees (per kW and MWh) can be set in the sheet >Project Setting<. Ensure that the prices and fees are not double counted (e.g grid fees is set in Sheet >Project Setting< AND is included here in the energy price, or the other way round is included in neither cells.
| 8 | Energy price for energy used by booster | 1 | 66 | 71 | 81.85 | 90.11 | 90.49 | 85.98 | 20 20: 66 | 1
| 8 | Energy price for energy used by booster | 2 | 63.45 | 70.7 | 70.59 | 80.45 | 79.25 | 75.52 | 20 20: 63.45 | 2
| 8 | Energy price for energy used by booster | 3 | 63.54 | 70.46 | 69.53 | 79.91 | 71.24 | 74.72 | 20 20: 63.54 | 3
| 8 | Energy price for energy used by booster | 4 | 61.82 | 69.74 | 64.4 | 79.29 | 70.67 | 71.845 | 20 20: 61.82 | 4
| 8 | Energy price for energy used by booster | 5 | 61.85 | 70.46 | 63.88 | 83.38 | 66.94 | 73.63 | 20 20: 61.85 | 5
| 8 | Energy price for energy used by booster | 6 | 61.75 | 73.91 | 63.62 | 91.38 | 62.09 | 77.5 | 20 20: 61.75 | 6
| 8 | Energy price for energy used by booster | 7 | 62.59 | 83.98 | 64.43 | 115.6 | 57.9 | 90.015 | 20 20: 62.59 | 7
| 8 | Energy price for energy used by booster | 8 | 66.9 | 106.64 | 60.53 | 110.72 | 46.35 | 85.625 | 20 20: 66.9 | 8
| 8 | Energy price for energy used by booster | 9 | 74.82 | 108.7 | 60.88 | 98.4 | 19.77 | 79.64 | 20 20: 74.82 | 9
| 8 | Energy price for energy used by booster | 10 | 77.9 | 87.21 | 55.38 | 81.43 | 4.24 | 68.405 | 20 20: 77.9 | 10
| 8 | Energy price for energy used by booster | 11 | 71.8 | 75.92 | 32.99 | 70 | 0 | 51.495 | 20 20: 71.8 | 11
| 8 | Energy price for energy used by booster | 12 | 70.77 | 72.02 | 36.96 | 58.75 | -0.05 | 47.855 | 20 20: 70.77 | 12
| 8 | Energy price for energy used by booster | 13 | 67.73 | 69.35 | 6.06 | 44.34 | -0.1 | 25.2 | 20 20: 67.73 | 13
| 8 | Energy price for energy used by booster | 14 | 68.78 | 69.29 | 0.28 | 36.5 | -1.05 | 18.39 | 20 20: 68.78 | 14
| 8 | Energy price for energy used by booster | 15 | 73.39 | 70.64 | -0.9 | 36.2 | -2.21 | 17.65 | 20 20: 73.39 | 15
| 8 | Energy price for energy used by booster | 16 | 79.11 | 72.26 | 0.75 | 42.54 | -2.05 | 21.645 | 20 20: 79.11 | 16
| 8 | Energy price for energy used by booster | 17 | 87.8 | 81.06 | 6.01 | 63.79 | -0.27 | 34.9 | 20 20: 87.8 | 17
| 8 | Energy price for energy used by booster | 18 | 94.93 | 100 | 58.22 | 77.34 | 22.61 | 67.78 | 20 20: 94.93 | 18
| 8 | Energy price for energy used by booster | 19 | 99.87 | 119.58 | 74.6 | 91.61 | 71.12 | 83.105 | 20 20: 99.87 | 19
| 8 | Energy price for energy used by booster | 20 | 91.57 | 119.25 | 89.36 | 121.02 | 99.5 | 105.19 | 20 20: 91.57 | 20
| 8 | Energy price for energy used by booster | 21 | 81.97 | 93.4 | 95.26 | 190.46 | 115.14 | 142.86 | 20 20: 81.97 | 21
| 8 | Energy price for energy used by booster | 22 | 75.74 | 80.15 | 91.07 | 120 | 115.44 | 105.535 | 20 20: 75.74 | 22
| 8 | Energy price for energy used by booster | 23 | 74.68 | 77.98 | 89.41 | 106.86 | 114.33 | 98.135 | 20 20: 74.68 | 23
| 8 | Energy price for energy used by booster | 24 | 69.13 | 74.34 | 88.46 | 91.55 | 99.79 | 90.005 | 20 20: 69.13 | 24
| 8 |  | Daily average | 73.6621 | 82.835 | 55.1508 | 85.9012 | 50.0475 | 70.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6621 | Daily average
8
Link to additional information / German translation | 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | Hour of day | Data centre operator / waste heat provider: Electricity price for active cooling system | [19 empty] | Hour of day
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system |  | EUR/MWh_elec
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system |  | Electricity price fo actice cooling system that has to be paid by the data centre operator (Contractor 2) if the heat is not be taken up by the district heating system (Contractor 1). Ensure that the efficiency defined in the Project Sheet is set accordingly. Be aware that grid fees (per MWh) can be set in the sheet >Project Setting<. Ensure that the prices and fees are not double counted (e.g grid fees is set in Sheet >Project Setting< AND is included here in the energy price, or the other way round is included in neither cells.
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 1 | 76 | 81 | 91.85 | 100.11 | 100.49 | 95.98 | 20 20: 100 | 1
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 2 | 73.45 | 80.7 | 80.59 | 90.45 | 89.25 | 85.52 | 20 20: 100 | 2
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 3 | 73.54 | 80.46 | 79.53 | 89.91 | 81.24 | 84.72 | 20 20: 100 | 3
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 4 | 71.82 | 79.74 | 74.4 | 89.29 | 80.67 | 81.845 | 20 20: 100 | 4
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 5 | 71.85 | 80.46 | 73.88 | 93.38 | 76.94 | 83.63 | 20 20: 100 | 5
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 6 | 71.75 | 83.91 | 73.62 | 101.38 | 72.09 | 87.5 | 20 20: 100 | 6
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 7 | 72.59 | 93.98 | 74.43 | 125.6 | 67.9 | 100.015 | 20 20: 100 | 7
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 8 | 76.9 | 116.64 | 70.53 | 120.72 | 56.35 | 95.625 | 20 20: 100 | 8
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 9 | 84.82 | 118.7 | 70.88 | 108.4 | 29.77 | 89.64 | 20 20: 100 | 9
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 10 | 87.9 | 97.21 | 65.38 | 91.43 | 14.24 | 78.405 | 20 20: 100 | 10
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 11 | 81.8 | 85.92 | 42.99 | 80 | 10 | 61.495 | 20 20: 100 | 11
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 12 | 80.77 | 82.02 | 46.96 | 68.75 | 9.95 | 57.855 | 20 20: 100 | 12
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 13 | 77.73 | 79.35 | 16.06 | 54.34 | 9.9 | 35.2 | 20 20: 100 | 13
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 14 | 78.78 | 79.29 | 10.28 | 46.5 | 8.95 | 28.39 | 20 20: 100 | 14
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 15 | 83.39 | 80.64 | 9.1 | 46.2 | 7.79 | 27.65 | 20 20: 100 | 15
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 16 | 89.11 | 82.26 | 10.75 | 52.54 | 7.95 | 31.645 | 20 20: 100 | 16
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 17 | 97.8 | 91.06 | 16.01 | 73.79 | 9.73 | 44.9 | 20 20: 100 | 17
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 18 | 104.93 | 110 | 68.22 | 87.34 | 32.61 | 77.78 | 20 20: 100 | 18
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 19 | 109.87 | 129.58 | 84.6 | 101.61 | 81.12 | 93.105 | 20 20: 100 | 19
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 20 | 101.57 | 129.25 | 99.36 | 131.02 | 109.5 | 115.19 | 20 20: 100 | 20
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 21 | 91.97 | 103.4 | 105.26 | 200.46 | 125.14 | 152.86 | 20 20: 100 | 21
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 22 | 85.74 | 90.15 | 101.07 | 130 | 125.44 | 115.535 | 20 20: 100 | 22
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 23 | 84.68 | 87.98 | 99.41 | 116.86 | 124.33 | 108.135 | 20 20: 100 | 23
| 9 | Data centre operator / waste heat provider: Electricity price for active cooling system | 24 | 79.13 | 84.34 | 98.46 | 101.55 | 109.79 | 100.005 | 20 20: 100 | 24
| 9 |  | Daily average | 83.6621 | 92.835 | 65.1508 | 95.9013 | 60.0475 | 80.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | Daily average
9
Link to additional information / German translation | 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | Hour of day | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | [19 empty] | Hour of day
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) |  | Share between 0% and 100%
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) |  | This is the required share of active cooling (as opposed to free cooling) required, if heat is not taken up by Contract 1 and the district heating system
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 1 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 1 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 2 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 2 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 3 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 3 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 4 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 4 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 5 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 5 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 6 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 6 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 7 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 7 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 8 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 8 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 9 | 0.2 | 0.7 | 0.7 | 1 | 1 | 1 | [14 empty] | 9 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 10 | 0.2 | 0.85 | 0.85 | 1 | 1 | 1 | [14 empty] | 10 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 11 | 0.35 | 0.85 | 0.85 | 1 | 1 | 1 | [14 empty] | 11 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 12 | 0.35 | 0.85 | 0.85 | 1 | 1 | 1 | [14 empty] | 12 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 13 | 0.35 | 0.85 | 0.85 | 1 | 1 | 1 | [14 empty] | 13 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 14 | 0.35 | 0.85 | 0.85 | 1 | 1 | 1 | [14 empty] | 14 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 15 | 0.35 | 0.85 | 0.85 | 1 | 1 | 1 | [14 empty] | 15 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 16 | 0.35 | 0.85 | 0.85 | 1 | 1 | 1 | [14 empty] | 16 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 17 | 0.2 | 0.85 | 0.85 | 1 | 1 | 1 | [14 empty] | 17 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 18 | 0.2 | 0.75 | 0.75 | 1 | 1 | 1 | [14 empty] | 18 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 19 | 0.2 | 0.75 | 0.75 | 1 | 1 | 1 | [14 empty] | 19 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 20 | 0.2 | 0.75 | 0.75 | 1 | 1 | 1 | [14 empty] | 20 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 21 | 0.2 | 0.75 | 0.75 | 1 | 1 | 1 | [14 empty] | 21 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 22 | 0.2 | 0.75 | 0.75 | 1 | 1 | 1 | [14 empty] | 22 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 23 | 0.2 | 0.75 | 0.75 | 1 | 1 | 1 | [14 empty] | 23 | bar: 20 20
| 10 | Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | 24 | 0.2 | 0.75 | 0.75 | 1 | 1 | 1 | [14 empty] | 24 | bar: 20 20
| 10 | Share of active cooling (=1 - Share of free cooling) | Daily average | 0.2375 | 0.76458 | 0.76458 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Daily average
|  |  |  | Winter day | Spring / fall weekday | Spring / fall weekend | Summer weekday | Summer weekend | Maintenance of HP | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
* Temperature heat pump sink in minus temperature drop (delta T heat exchanger) between temperature heat pump sink in and return point DH network

## Definition of Typical Year
Go to Content
Colour Code | Header
Item / unit
User input
| Cell with formula |  | Cell with formula
Go to Content
Input - not used for calculation
Control cells
Check settings / input data, there might be some error
[5 empty] | Technical parameters | [14 empty] | Economic Parameters Contractor 1 / DH Operator | [9 empty] | Economic parameters Contractor 2 / Data centre Operator
| Typical days | Name of typical day | Weight of typical day | Days of Typical Day in Typical Year | Average Flow Temperature of data centre cooling system | Average flow temperature HP, source in | Average DH supply line temperature | Average Required Temperature Sink Out | Average DH return line temperature | Average Temperature Heat Pump Sink In | Hours of Operation per day | Hours of operation (full load hour equivalents) per day | Available heat from DC per day | Used heat from DC per day | Electricity used by Heat pump per day | Fuel used by Booster per day | Heat provided to the grid per day | Avoided Electricity demand for cooling | Remaining Electricity demand for cooling | Waste heat costs in case of pay-as-you-go contract based on negotiated price p_1 between Contractor 1 and Contractor 2 | Electricity cost HP per day | Electricity costs auxiliary energy | Fuel costs Booster per day | Variable O&M costs HP per day | Variable O&M costs Booster per day | Total variable costs per day excluding subsidies | Subsidies for utilized waste heat provided by DC | Avoided costs of alternative production that has been replaced by waste heat utilisation | Waste heat costs in case of Take-or-pay contract based on negotiated price p_1 between Contractor 1 and Contractor 2 | Avoided electricity costs due to reduced active cooling | Remaining electricity costs for active cooling | Energy costs based on p_0 for waste heat from DC (always Take-or-Pay contract type) | Variable O&M costs | Waste heat earnings in case of pay-as-you-go contract based on negotiated price p_1 between Contractor 1 and Contractor 2 | Waste heat earnings in case of Take-or-pay contract based on negotiated price p_1 between Contractor 1 and Contractor 2
| - |  | % | days | °C | °C | °C | °C | °C | °C | hours / day | hours / day | MWh_th / day | MWh_th / day | MWh_el / day | MWh / day | MWh_th / day | MWh / day | MWh / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day | EUR / day
|  | Labels each characteristic day (e.g. Winter day, Summer weekend) | Relative share of typical day in analysed typical year. Shares will be scaled automatically to 100% (365 days per year), if total sum of shares don't sum up to 100% | Number of days that each typical day represents across the entire year | Flow Temperature of the cooling system of the DC | Flow Temperature HP equals the temperature of the cooling system reduced by delta T of the heat exchanger | The required supply temperature for the district heating grid. | Temperature required by the DH grid and needs to be provided by HP + booster (may be higher than what HP alone can deliver). | The return temperature of the district heating network. | Inlet temperature into the heat pump from the sink (DH side). | Number of hours the system is running per day | Number of full-load-hour equivalents per day (MWh_th provided by heat pump / heat pump capacity) | Total thermal energy (waste heat) available from the data centre on that typical day | Amount of the available waste heat that is actually used in the system (e.g. heat pump) | Amount of electricity consumed by the heat pump to extract and upgrade the waste heat | If additional heating is needed, this reflects the fuel consumption of a booster heater | Total heat delivered to the district heating grid, coming from both the heat pump and booster | Total AVOIDED electricity due to less active cooling needs. (THIS ARE SAVINGS) | Total remaining electricity demand for active cooling | Daily cost for the waste heat based on a variable (usage-based) contract with a negotiated price. These Waste heat costs are part of SRMC. | Total electricity cost for operating the heat pump on that day | Electricity costs associated with additional or auxiliary components of the system (not the HP) (so SRMC) | Cost of fuel used by the booster to supplement heating if necessary | Operating and maintenance costs that vary with usage, associated with the heat pump. | Operating and maintenance costs that vary with usage, associated with the booster unit. | Sum of all daily variable costs (electricity, fuel, O&M), excluding any subsidies. | Daily subsidies received for using waste heat from the data centre. Considered as earnings. | Costs saved by not using an alternative (usually more expensive) heat production method. Considered as earnings. | Daily cost under a fixed contract where the buyer pays for a set amount of heat, used or not. These Waste heat costs are NOT part of SRMC. | Total hourly REDUCED electricity costs due to less active cooling needs. (THIS ARE SAVINGS) | Total hourly remaining electricity costs for active cooling | Waste heat cost based on price p_0 that is paid at the border between data centre cooling and waste heat recovery system under Take-or-Pay conditions | These are the operation and maintenance costs that vary depending on how much of the heat recovery system is used | Revenue generated for the data centre based on actual usage and negotiated price. These waste heat costs are part of SRMC. | Guaranteed revenue for the data centre based on fixed contractual payments.
| 1 | Winter day | 25 | 94.6086 | 40 | 37 | 82.4306 | 85.4306 | 45 | 48 | 24 | 22.7874 | 48 | 48 | 20.3622 | 0.50683 | 68.1753 | 1.52 | 0 | 0 | 1722.2343 | 185.9327 | 38.8386 | 0 | 0 | 1947.0056 | 0 | 4431.3962 | 96 | 126.7507 | 0 | 0 | 96 | 0 | 96
| 2 | Spring / fall weekday | 33.5 | 126.7755 | 40 | 37 | 83.125 | 86.125 | 45 | 48 | 24 | 22.8515 | 48 | 48 | 20.5545 | 0 | 67.8689 | 4.8933 | -4.1448e-17 | 0 | 1927.4058 | 97.3474 | 0 | 0 | 0 | 2024.7531 | 0 | 4072.1369 | 96 | 452.8068 | -4.9199e-15 | 0 | 96 | 0 | 96
| 3 | Spring / fall weekend | 13.4 | 50.7102 | 40 | 37 | 83.125 | 86.125 | 45 | 48 | 24 | 22.8515 | 48 | 48 | 20.5545 | 0 | 67.8689 | 4.8933 | -4.1448e-17 | 0 | 1381.3092 | 97.3474 | 0 | 0 | 0 | 1478.6566 | 0 | 4072.1369 | 96 | 309.3287 | -2.9379e-15 | 0 | 96 | 0 | 96
| 4 | Summer weekday | 17 | 64.3339 | 40 | 37 | 60 | 63 | 45 | 48 | 23 | 16.2635 | 48 | 36.4133 | 12.3771 | 0 | 48.3025 | 4.8551 | 1.5449 | 0 | 1143.086 | 58.5484 | 0 | 0 | 0 | 1201.6344 | 0 | 1932.0986 | 96 | 443.5394 | 170.2286 | 0 | 72.8266 | 0 | 96
| 5 | Summer weekend | 6.8 | 25.7335 | 40 | 37 | 60 | 63 | 45 | 48 | 24 | 16.9706 | 48 | 37.9965 | 12.9152 | 0 | 50.4026 | 5.0662 | 1.3338 | 0 | 788.4402 | 61.094 | 0 | 0 | 0 | 849.5342 | 0 | 2772.1414 | 96 | 304.2126 | 80.0914 | 0 | 75.993 | 0 | 96
| 6 | Maintenance of HP | 0.75 | 2.8383 | 40 | 37 | 71.5625 | 74.5625 | 45 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7 | 7 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 9 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10 | 10 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11 | 11 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 12 | 12 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 13 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 14 | 14 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 15 | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 16 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 17 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 18 | 18 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 19 | 19 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 20 | 20 | 0 | 0 | 30 | 27 | 83.3056 | 86.3056 | 43.125 | 46.125 | 0 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0.0032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048 | 0 | 0.32 | 0 | 0 | 0 | 0.048
|  |  | 96.45 | 365 | Independent of actual operation, different formular | Independent of actual operation, different formular | Independent of actual operation, different formular | Independent of actual operation, different formular | Independent of actual operation, different formular | Independent of actual operation, different formular | Independent of actual operation, different formular | Independent of actual operation, different formular | Independent of actual operation, different formular | [15 empty] | Independent of actual operation, different formular |  |  | Independent of actual operation, different formular
|  |  |  | References Control ASSERT WAHR/TRUE | 6480 | 5976 | 12565.1667 | 14005.1667 | 7515 | 8955 | 119 | 101.7244 | 240.024 | 218.4098 | 86.7634 | 0.50683 | 302.6183 | 21.228 | 2.8819 | 0 | 6962.4755 | 500.2699 | 38.8386 | 0 | 0 | 7501.5841 | 0 | 17279.91 | 480.048 | 1636.6382 | 250.64 | 0 | 436.8196 | 0 | 480.048
[5 empty] | Flow temperature of data centre cooling system | Flow Temperature HP | DH supply line temperature | Required temperature sink out | DH return line temperature | Temperature heat pump sink in | Operation hours | Operation hours in full-load-hours equivalents | Available waste heat (DC heat source) | Waste heat input from DC | Electricity input for heat pump | Energy input for booster | Total heat output after considering restriction imposed by heat demand | Avoided electricity demand due to reduced active cooling | Remaining electricity demand for active cooling | Energy costs p_1 for waste heat from DC as taken (Pay-as-you-go) (Contractor 1) | Electricity costs for heat pump (Contractor 1) | Electricity costs auxiliary energy (Contractor 1) | Fuel costs for booster (Contractor 1) | Variable (MWh-specific) O&M Costs Heat pump Contractor 1 / DH Operator | Variable (MWh-specific) O&M Costs Booster Contractor 1 / DH Operator | Short run marginal costs per hour Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Subsidies given per utilized waste heat to Contractor 1 / DH Operator considering that they must not exceed costs for electricity | Reference SRMC alternative production [EUR/h] | Energy costs p_1 for waste heat from DC as provided by DC (take-or-pay) (Contractor 1) | Avoided electricity costs due to reduced active cooling | Remaining electricity costs for active cooling | Energy costs p_0 for waste heat from DC | Variable O&M costs for heat recovery system operator | Energy costs p_1 for waste heat from DC as taken (Pay-as-you-go) (Contractor 1) | Energy costs p_1 for waste heat from DC as provided by DC (take-or-pay) (Contractor 1)
[5 empty] | 6480 | 5976 | 12565.1667 | 14005.1667 | 7515 | 8955 | 119 | 101.7244 | 240.024 | 218.4098 | 86.7634 | 0.50683 | 302.6183 | 21.228 | 2.612 | 0 | 6962.4755 | 500.2699 | 38.8386 | 0 | 0 | 7501.5841 | 0 | 17279.91 | 480.048 | 1636.6382 | 196.864 | 0 | 436.8196 | 0 | 480.048
[5 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE

## Main Results - IRR DC Operator
Go to Content
Colour Code | Header | [11 empty] | Max. waste heat load available: 2 MW
| Item / unit | [11 empty] | T source HP, out: 28 °C | 28 | P th_nominal_out: 3MW_th
| User input | [11 empty] | T source, in: 40 °C | 40 | COP nom.: 3 at
| Cell with formula | [11 empty] | T source HP, in: 37 °C | 37
| Go to Content | [11 empty] | T sink HP, in: 48 °C | 48 | P th: 0.5 MW_th
| Input - not used for calculation | [11 empty] | T sink HP, out: 80.1 °C | 80.1
[13 empty] | T supply line DH: 77.1 °C | 77.1
| Control cells | [11 empty] | T return line DH: 45 °C | 45
| Check settings / input data, there might be some error | [11 empty] | HEx 1, Delta T: 3 K
HEx 2, Delta T: 3 K
| Economics of waste heat recovery system (B1 - B2) | [11 empty] | Price p_0 (paid to external entity): 0 [EUR/MWh_heat_provided_by_DC] | 0
[13 empty] | Negotiated price p_1: 2 [EUR/MWh_heat_provided_by_DC] | 2 | [EUR/MWh_heat_provided_by_DC]
| Contract type between Contractor 1 and Contractor 2 | Take-or-pay |  |  | 1 | Select contract type: waste heat sold by DC based on (1) take-or-pay contract or (2) pay-as-you-go (utilised heat) | [6 empty] | Contract type: Take-or-pay | 1 | Take-or-pay
| Negotiated energy price p_1 | [EUR/MWh_heat_provided_by_DC] |  |  | 2 | Price p_1 for waste heat from DC between Contractor 1 / DH operator and Contractor 2 / DC operator. These are costs for Contractor 1 / DH operator and revenues for Contractor 2 / DC operator. |  |  |  | Expected IRR of Contractor 1 / DH operator cannot be met
| Energy price p_0 paid to external entity | Take-or-pay [EUR/MWh_waste_heat_provided] |  |  | 0 | Price p_0 represents the payment for waste heat from the data centre to an external third party. This cost is not considered as revenue for either Contractor 1 or Contractor 2 / DH operator price | [6 empty] | Expected IRR of Contractor 1 / DH operator cannot be met | -3.1672
[13 empty] | Expected IRR of Contractor 1 / DH operator is not met. | IRR too low |  | 0.019762
| Total investment |  |  |  | Share paid by Contractor 1 |  | Annual operation independent O&M expenses |  |  |  | Share paid by Contractor 1 | Energy | Waste heat supplied by the DC: 17.38 GWh/yr | 17.3838 |  | 5%
| Investment costs: equipment, installation, heat exchangers |  | EUR | 500000 | 0% |  | Regular annual expenses |  | EUR/yr | 50000 | 0% |  | Waste heat utilised in the HP: 16.38 GWh/yr | 16.3809
| Heat network |  | EUR | 126000 | 0% |  | Cost for waste heat p_0 (Take-or-pay contract) |  | EUR/yr | 0 | 0% |  | Heat fed into grid: 22.9 GWh/yr | 22900.2635
| Planning |  | EUR | 50080 | 0%
| Total |  | EUR | 676080 |  |  | Total annual operation independent expenses |  | EUR/yr | 50000 |  |  | Electricity input HP: 6.7 GWh/yr | 6.7032
[13 empty] | Electricity / fuel input booster: 0.05 GWh/yr | 47.9508
| CAPEX investment subsidies |  |  |  | Share received by Contractor 1 |  | Annual variable costs |  |  |  | Share paid by Contractor 1 |  | Annual SCOP heat pump: 3.44 | 3.4438
| Total subsidies |  | EUR | 0 | 0% |  | Variable O&M costs per year |  | EUR/yr | 32761.8431 | 0%
| Total |  | EUR | 0 |  |  | Total annual operation dependent expenses |  | EUR/yr | 32761.8431
Price based on the short-run marginal costs of alternative heat production: 58.41 EUR/MWh_fed_into_DH_grid
| Costs paid by Contractor 2 / DC operator |  |  |  | Share | Total costs | Costs paid by Contractor 1 / DH operator |  |  | Share
| Investments |  | EUR | 676080 | 100% | 676080 |  | EUR | 0 | 0%
| Annual operation independent O&M expenses |  | EUR/yr | 50000 | 100% | 50000 |  | EUR/yr | 0 | 0%
| Annual variable costs |  | EUR/yr | 32761.8431 | 100% | 32761.8431 |  | EUR/yr | 0 | 0% |  | Contractor 2 / DC operator: | Break-even price for waste heat supplied by DC: 1.52 EUR/MWh_provided_by_DC | 1.5216
[13 empty] | Break-even price for waste heat utilised by HP: 1.61 EUR/MWh_utilized_by_HP | 1.6148
| Total annual expenses (excluding annualised investments) |  | EUR/yr | 82761.8431
| Annual earnings (under negotiated price p1) |  | EUR/yr | 34767.5272
| Annual reduced electricity costs for active cooling |  | EUR/yr | 121445.7164 |  | Expected IRR of Contractor 1 / DH operator is not met.
[12 empty] | Investments | Contractor 2's total investment needs (incl. subsidies, incl. cost share of heat recovery): 676.08 kEUR
| IRR of Contractor 2 / DC Operator |  |  | 6.83 % | [7 empty] | Costs | Contractor 2's annual O&M expenses: 82.8 kEUR (excl. annualised investment costs)
| Considering an underlying lifetime of 15 years for Contractor 2 / DC Operator | [11 empty] | Contractor 2's total annual expenses: 147.9 kEUR (incl. annualised investment costs)
| Break-even price for Contractor 2 / DC Operator |  | Break-even price for waste heat supplied by DC: 1.52 EUR/MWh_provided_by_DC Break-even price for waste heat utilised by HP: 1.61 EUR/MWh_utilized_by_HP
[13 empty] | Annual operation hours: 8628 h/yr (359.5 days/yr), annual full load hours: 7695 h/yr | 8628 | 7695 | 359.5
Contractor 2's net earnings per MWh of heat supplied: 0.5 EUR/MWh_provided_by_DC
Contractor 2's net earnings due to heat sold to contractor 1 and reduced electricity costs for cooling: 8.3 kEUR/yr (considering annualised investment costs)
[13 empty] | Contractor 2's gross earnings due to heat sold to contractor 1: 34.8 kEUR/yr | 34.8
[13 empty] | Contractor 2's avoided electricity costs for active cooling due to heat sold to contractor 1: 121.4 kEUR/yr | 121.4
Total costs for heat recovery system
[13 empty] | Investments (considering subsidies): 676.1 kEUR (lump-sum) | 676080 | 1
[13 empty] | Annual operation independent expenses: 50 kEUR/yr | 50000 | 1
[13 empty] | Annual variable costs: 32.8 kEUR/yr | 32761.8431 | 1
Share paid by Contractor 1 / DH operator
[13 empty] | Investments (considering subsidies): 0 kEUR (lump-sum) | 0 | 0 %
[13 empty] | Annual operation independent expenses: 0 kEUR/yr | 0 | 0 %
[13 empty] | Annual variable costs: 0 kEUR/yr | 0 | 0 %
Share paid by Contractor 2 / DC operator
[13 empty] | Investments (considering subsidies): 676.1 kEUR (lump-sum) | 676080 | 100 %
[13 empty] | Annual operation independent expenses: 50 kEUR/yr | 50000 | 100 %
[13 empty] | Annual variable costs: 32.8 kEUR/yr | 32761.8431 | 100 %
[13 empty] | Total annualised costs (considering demanded IRR and depreciation time of contractor 2): 147.9 kEUR/yr | 147.8969
[13 empty] | Contractor 1's internal rate of return: 1.98 % per year (considering calculatory life time of 15 years) | 1.98 %
[13 empty] | Contractor 2's internal rate of return: 6.83 % per year (considering calculatory life time of 15 years) | 6.83 %
[13 empty] | Investments (considering subsidies): 0 kEUR (lump-sum) | 0 | 0 %
[13 empty] | Annual operation independent expenses: 0 kEUR/yr | 0 | 0 %
[13 empty] | Annual variable costs: 0 kEUR/yr | 0 | 0 %
Share paid by Contractor 2 / DC operator
[13 empty] | Investments (considering subsidies): 676.1 kEUR (lump-sum) | 676080 | 100 %
[13 empty] | Annual operation independent expenses: 50 kEUR/yr | 50000 | 100 %
[13 empty] | Annual variable costs: 32.8 kEUR/yr | 32761.8431 | 100 %
[13 empty] | Total annualised costs (considering demanded IRR and depreciation time of contractor 2 / DC operator): 147.9 kEUR/yr | 147.8969
[13 empty] | Avoided electricity demand for active cooling: 1.5 GWh/yr | 1.455 | GWh/yr
[13 empty] | Remaining electricity demand for active cooling: 0.1 GWh/yr | 0.13371 | GWh/yr
[13 empty] | Avoided electricity costs for active cooling: 121.4 kEUR/yr | 121.4457 | kEUR/yr
[13 empty] | Remaining electricity costs for active cooling: 13 kEUR/yr | 13.0125 | kEUR/yr
Price based on the short-run marginal costs of alternative heat production: 58.41 EUR/MWh_fed_into_DH_grid
PRICES0
OUTPUT CONTRACTOR 2
Heat pump
HEx 2: Heat exchanger & piping
Booster
DH grid / heat sink
HEx 1: Heat exchanger & piping
T source HP, out: 28 °C
T sink HP, out: 80.1 °C
T sink HP, in: 48 °C
Annual SCOP heat pump: 3.44
T source, in: 40 °C
Data centre / waste heat source
Negotiated price p_1: 2 [EUR/MWh_heat_provided_by_DC]
Contract type: Take-or-pay
Price p_0 (paid to external entity): 0 [EUR/MWh_heat_provided_by_DC]
Max. waste heat load available: 2 MW
Costs paid by Contractor 2 / DC operator
Costs paid by Contractor 1 / DH operator
Investments (considering subsidies): 676.1 kEUR (lump-sum)
Annual operation independent expenses: 50 kEUR/yr
Annual variable costs: 32.8 kEUR/yr
Investments (considering subsidies): 676.1 kEUR (lump-sum)
Annual operation independent expenses: 50 kEUR/yr
Annual variable costs: 32.8 kEUR/yr
100 %
100 %
100 %
0 %
0 %
0 %
Electricity costs for active cooling
P th: 0.5 MW_th
P th_nominal_out: 3MW_th
Waste heat supplied by the DC: 17.38 GWh/yr
Waste heat utilised in the HP: 16.38 GWh/yr
Electricity / fuel input booster: 0.05 GWh/yr
Heat fed into grid: 22.9 GWh/yr
INVESTMENT
Contractor 2's total investment needs (incl. subsidies, incl. cost share of heat recovery): 676.08 kEUR
COSTS
Contractor 2's annual O&M expenses: 82.8 kEUR (excl. annualised investment costs)
Contractor 2's total annual expenses: 147.9 kEUR (incl. annualised investment costs)
IRR
Contractor 2's internal rate of return: 6.83 % per year (considering calculatory life time of 15 years)
BREAK-EVEN
Break-even price for waste heat supplied by DC: 1.52 EUR/MWh_provided_by_DC
Break-even price for waste heat utilised by HP: 1.61 EUR/MWh_utilized_by_HP
Investments (considering subsidies): 0 kEUR (lump-sum)
Annual operation independent expenses: 0 kEUR/yr
Annual variable costs: 0 kEUR/yr
Remaining electricity demand for active cooling: 0.1 GWh/yr
Avoided electricity demand for active cooling: 1.5 GWh/yr
Total annualised costs (considering demanded IRR and depreciation time of contractor 2): 147.9 kEUR/yr
Avoided electricity costs for active cooling: 121.4 kEUR/yr
Remaining electricity costs for active cooling: 13 kEUR/yr
EARNINGS
Contractor 2's net earnings due to heat sold to contractor 1 and reduced electricity costs for cooling: 8.3 kEUR/yr (considering annualised investment costs)
Contractor 2's net earnings per MWh of heat supplied: 0.5 EUR/MWh_provided_by_DC
Contractor 2's gross earnings due to heat sold to contractor 1: 34.8 kEUR/yr
Avoided electricity costs for active cooling: 121.4 kEUR/yr
Contractor 2's avoided electricity costs for active cooling due to heat sold to contractor 1: 121.4 kEUR/yr
T source HP, in: 37 °C
HEx 1, Delta T: 3 K
T return line DH: 45 °C
T supply line DH: 77.1 °C
INPUT
Contractor 2 / Data Centre Operator / Waste Heat Provider
Waste Heat Recovery System Ownership / Responsibilities / Cost allocation between Contractor 1 and 2 to be dicscussed and defined.
Contractor 1 / District Heating Operator:
Heat utilisation
Existing Heat Network / District Heating Operator
Actor
B1
B2
B3
Annual operation hours: 8628 h/yr (359.5 days/yr), annual full load hours: 7695 h/yr
Contractor 2's internal rate of return: 6.83 % per year (considering calculatory life time of 15 years)
Contractor 2's gross earnings due to heat sold to contractor 1: 34.8 kEUR/yr
Electricity input HP: 6.7 GWh/yr
Heat losses after heat pump = 1 %
HEx 2, Delta T: 3 K

## Main Results Extended
Go to Content
Colour Code | Header | [11 empty] | Max. waste heat load available: 2 MW
| Item / unit | [11 empty] | T source, out: 28 °C | P th_nominal_out: 3MW_th
| User input | [11 empty] | T source, in: 25 °C | COP nom.: 3 at
| Cell with formula | [11 empty] | T sink, in: 60 °C | P th: 0.5 MW_th
| Go to Content | [11 empty] | T sink, out: 90 °C
Input - not used for calculation
| Not used any more: relevant for future works - do not change | [11 empty] | Price p_0 (paid to external entity): 0 [EUR/MWh_heat_provided_by_DC] | 0
| Control cells | [11 empty] | Negotiated price p_1: 2 [EUR/MWh_heat_provided_by_DC] | 2 | [EUR/MWh_heat_provided_by_DC]
| Check settings / input data, there might be some error | [11 empty] | Contract Type: Take-or-pay | 1 | Take-or-pay
[12 empty] | Energy | Waste heat supplied by the DC: 17.38 GWh/yr
!! The section on 'Economics of heat recovery' of this sheet is for information purposes only. Please do not modify this worksheet !!
Economics of heat recovery
DO NOT CHANGE VALUES IN THIS SHEET BUT IN SHEET >Main Results - IRR DC Operator<
| Contract type between Contractor 1 and Contractor 2 | Take-or-pay |  |  | 1 | Select contract type: Waste heat sold by DC based on (1) take-or-pay contract or (2) pay-as-you-go (utilised heat)
| Negotiated energy price p_1 | [EUR/MWh_heat_provided_by_DC] |  |  | 2 | Price p_1 for waste heat from DC between Contractor 1 / DH operator and Contractor 2 / data centre operator. These are costs for Contractor 1 / DH operator and earnings for Contractor 2 / DC operator.
| Energy price p_0 paid to external entity | Take-or-pay |  |  | 0 | Price p_0 for waste heat from DC paid to external party. These are neither earnings for Contractor 1 nor Contractor 2 / DH operator
| Total investment |  |  |  | Share paid for by Contractor 1 |  | Annual operation independent O&M expenses |  |  |  | Share paid for by Contractor 1
| Investment costs: equipment, installation, heat exchangers |  | EUR | 500000 | 0% |  | Regular annual expenses |  | EUR/yr | 50000 | 0%
| Heat network |  | EUR | 126000 | 0% |  | Cost for waste heat p_0 (Take-or-pay contract) |  | EUR/yr | 0 | 0%
| Planning |  | EUR | 50080 | 0%
| Total |  | EUR | 676080 |  |  | Total annual operation independent expenses |  | EUR/yr | 50000
| CAPEX Investment subsidies |  |  |  | Share received by Contractor 1 |  | Annual variable costs |  |  |  | Share paid for by Contractor 1
| Total subsidies |  | EUR | 0 | 0% |  | Variable O&M costs per year |  | EUR/yr | 32761.8431 | 0%
| Total |  | EUR | 0 |  |  | Total annual operation dependent expenses |  | EUR/yr | 32761.8431
| Costs paid for by Contractor 2 / DC operator |  |  |  | Total costs |  | Costs paid for by Contractor 1 / DH operator
| Investments |  | EUR | 676080 | 676080 |  | Investments |  | EUR | 0
| Annual operation independent O&M expenses |  | EUR/yr | 50000 | 50000 |  | Annual operation independent O&M expenses |  | EUR/yr | 0
| Annual variable costs |  | EUR/yr | 32761.8431 | 32761.8431 |  | Annual variable costs |  | EUR/yr | 0
| Total annual expenses (excluding annualized investments) |  | EUR/yr | 82761.8431
| Annual earnings (under negotiated price p_1) |  | EUR/yr | 34767.5272
| Annual reduced electricity costs for active cooling |  | EUR/yr | 121445.7164
| 6.83 % |  | Internal Rate of Return |  |  |  |  | 1.98 %
| Considering an underlying lifetime of 15 years for Contractor 2 | [6 empty] | Considering an underlying lifetime of 15 years for Contractor 1
Waste heat utilized in the HP: 16.38 GWh/yr
[13 empty] | Heat fed into grid: 22.9 GWh/yr | 22900.2635
Electricity input HP: 6.7 GWh/yr
[13 empty] | Electricity / fuel input booster: 0.05 GWh/yr | 47.9508
Price based on the short-run marginal costs of alternative heat production: 58.41 EUR/MWh_fed_into_DH_grid
[12 empty] | Contractor 1 / DH Operator: | Break-even price for waste heat supplied by DC: -3.17 EUR/MWh_provided_by_DH
Break-even price for waste heat utilised by HP: -3.36 EUR/MWh_utilised_by_HP
Break-even price for waste heat fed into DH grid: -2.4 EUR/MWh_fed_into_grid
[12 empty] | Contractor 2 / DC Operator: | Break-even price for waste heat supplied by DC: 1.52 EUR/MWh_provided_by_DC | 1.5216
[13 empty] | Break-even price for waste heat utilised by HP: 1.61 EUR/MWh_utilized_by_HP | 1.6148
[12 empty] | Investments | Contractor 2's total investment needs (incl. subsidies, incl. cost share of heat recovery): 676.08 kEUR
Contractor 1's total Investment needs (incl. subsidies, incl. cost share of heat recovery): 4815 kEUR
[12 empty] | Costs | Contractor 2's annual expenses: 82.8 kEUR (excl. annualised investment costs)
Contractor 2's total annual expenses: 147.9 kEUR (incl. annualised investment costs)
[12 empty] | Costs | Contractor 1's total annual operation costs (incl. payments for heat to Contractor 2): 963.6 kEUR (incl. annual subsidies, excl. annualised investment costs)
Contractor 1's annual operation costs (excl. payments for heat to Contractor 2): 928.8 kEUR (incl. annual subsidies, excl. annualised investment costs)
Contractor 1's annual payments for heat to Contractor 2: 34.8 kEUR
Contractor 1's total annual expenses: 1427.5 kEUR (incl. annual subsidies, incl. annualised investment costs)
[13 empty] | Contractor 1's investments (incl. subsidies, excl. cost share of heat recovery): 4815 kEUR (lump-sum) | 4815000
[13 empty] | Contractor 1's annual operation independent expenses (excl. cost share of heat recovery): 348.5 kEUR/yr | 348525.103
[13 empty] | Contractor 1's annual variable costs (excl. cost share of heat recovery): 615 kEUR/yr | 615042.9291
[12 empty] | Earnings | Contractor 1's gross earnings based on avoided alternative heat production costs: 1337.6 kEUR/yr
[13 empty] | Contractor 1's net earnings per MWh supplied to grid (considering annual Inv. and O&M cost): -3.9 EUR/MWh_supplied_to_grid | -3.9225
[13 empty] | Contractor 1's net earnings per MWh waste heat provided by DC (considering annual Inv. and O&M cost): -5.2 EUR/MWh_provided_by_DC | -5.1672
[13 empty] | Contractor 1's net earnings per year (considering annual Inv. and O&M cost): -89.8 kEUR/yr | -89825.3272
Contractor 2's net earnings per MWh of heat supplied: 0.5 EUR/MWh_provided_by_DC
Contractor 2's net earnings per year due to heat sold to contractor 1: 8.3 kEUR/yr (considering annualized investment costs)
[13 empty] | Contractor 2's gross earnings per year due to heat sold to contractor 1: 34.8 kEUR/yr | 34.8
Total costs for heat recovery system
[13 empty] | Investments (considering subsidies): 676.1 kEUR (lumpsum) | 676080 | 1
[13 empty] | Annual operation independent expenses: 50 kEUR/yr | 50000 | 1
[13 empty] | Annual variable costs: 32.8 kEUR/yr | 32761.8431 | 1
Share paid by Contractor 1 / DH operator
[13 empty] | Investments (considering subsidies): 0 kEUR (lumpsum) | 0 | 0 %
[13 empty] | Annual operation independent expenses: 0 kEUR/yr | 0 | 0 %
[13 empty] | Annual variable costs: 0 kEUR/yr | 0 | 0 %
Share paid by Contractor 2 / DC operator
[13 empty] | Investments (considering subsidies): 676.1 kEUR (lumpsum) | 676080 | 100 %
[13 empty] | Annual operation independent expenses: 50 kEUR/yr | 50000 | 100 %
[13 empty] | Annual variable costs: 32.8 kEUR/yr | 32761.8431 | 100 %
[13 empty] | Total annualised costs (considering demanded IRR and depreciation time of contractor 2 / DC operator): 147.9 kEUR/yr | 147.8969
[13 empty] | Contractor 1 / DH operator: Internal rate of return: 1.98 % (considering calculatory life time of 15 years) | 1.98 %
[13 empty] | Contractor 2 / DC operator: Internal rate of return: 6.83 % (considering calculatory life time of 15 years) | 6.83 %
[13 empty] | Avoided electricity demand for active cooling: 1.5 GWh/yr | 1.455 | GWh/yr
[13 empty] | Remaining electricity demand for active cooling: 0.1 GWh/yr | 0.13371 | GWh/yr
[13 empty] | Avoided electricity costs for active cooling: 121.4 kEUR/yr | 121.4457 | kEUR/yr
[13 empty] | Remaining electricity costs for active cooling: 13 kEUR/yr | 13.0125 | kEUR/yr
Price based on the short-run marginal costs of alternative heat production: 58.41 EUR/MWh_fed_into_DH_grid
Break-even price for waste heat supplied by DC: -3.17 EUR/MWh_provided_by_DH
Break-even price for waste heat utilised by HP: -3.36 EUR/MWh_utilised_by_HP
Break-even price for waste heat fed into DH grid: -2.4 EUR/MWh_fed_into_grid
PRICES0
Avoided electricity costs for active cooling: 121.4 kEUR/yr
1
2
3
EARNINGS
Contractor 1's gross earnings based on avoided alternative heat production costs: 1337.6 kEUR/yr
Contractor 2's gross earnings per year due to heat sold to contractor 1: 34.8 kEUR/yr
INPUT
Contractor 2 / Data centre operator
Waste heat recovery system Ownership / responsibilities / cost allocation between contractor 1 and 2 to be dicscussed and defined.
Contractor 1 / District heating operator: heat utilisation
District heating operator
Heat pump
Heat exchanger & piping
Booster
DH grid / heat sink
Data centre / heat source
Heat exchanger & piping
T source, out: 28 °C
T sink, out: 90 °C
T sink, in: 60 °C
COP nom.: 3 at
T source, in: 25 °C
Negotiated price p_1: 2 [EUR/MWh_heat_provided_by_DC]
Contract Type: Take-or-pay
Price p_0 (paid to external entity): 0 [EUR/MWh_heat_provided_by_DC]
Heat losses after heat pump = 1 %
Max. waste heat load available: 2 MW
Costs paid by Contractor 2 / DC operator
Costs paid by Contractor 1 / DH operator
Investments (considering subsidies): 676.1 kEUR (lumpsum)
Annual operation independent expenses: 50 kEUR/yr
Annual variable costs: 32.8 kEUR/yr
Investments (considering subsidies): 0 kEUR (lumpsum)
Annual operation independent expenses: 0 kEUR/yr
Annual variable costs: 0 kEUR/yr
Investments (considering subsidies): 676.1 kEUR (lumpsum)
Annual operation independent expenses: 50 kEUR/yr
Annual variable costs: 32.8 kEUR/yr
100 %
100 %
100 %
0 %
0 %
0 %
Contractor 2's gross earnings per year due to heat sold to contractor 1: 34.8 kEUR/yr
Contractor 2 / DC operator: Internal rate of return: 6.83 % (considering calculatory life time of 15 years)
T sink, out: 90 °C
P th: 0.5 MW_th
P th_nominal_out: 3MW_th
Total annualised costs (considering demanded IRR and depreciation time of contractor 2 / DC operator): 147.9 kEUR/yr
Waste heat supplied by the DC: 17.38 GWh/yr
Waste heat utilized in the HP: 16.38 GWh/yr
Electricity input HP: 6.7 GWh/yr
Electricity / fuel input booster: 0.05 GWh/yr
ENERGY
Heat fed into grid: 22.9 GWh/yr
Contractor 1's total Investment needs (incl. subsidies, incl. cost share of heat recovery): 4815 kEUR
Contractor 2's total investment needs (incl. subsidies, incl. cost share of heat recovery): 676.08 kEUR
INVEST-
MENT
Contractor 2's annual expenses: 82.8 kEUR (excl. annualised investment costs)
Contractor 1's total annual operation costs (incl. payments for heat to Contractor 2): 963.6 kEUR (incl. annual subsidies, excl. annualised investment costs)
ANNUAL
COSTS
Contractor 1's annual operation costs (excl. payments for heat to Contractor 2): 928.8 kEUR (incl. annual subsidies, excl. annualised investment costs)
Contractor 1's annual payments for heat to Contractor 2: 34.8 kEUR
Contractor 2's total annual expenses: 147.9 kEUR (incl. annualised investment costs)
Contractor 1's total annual expenses: 1427.5 kEUR (incl. annual subsidies, incl. annualised investment costs)
COSTS
EARNINGS
Contractor 1's net earnings per year (considering annual Inv. and O&M cost): -89.8 kEUR/yr
Contractor 2's net earnings per year due to heat sold to contractor 1: 8.3 kEUR/yr (considering annualized investment costs)
EARNINGS
Contractor 1's net earnings per MWh waste heat provided by DC (considering annual Inv. and O&M cost): -5.2 EUR/MWh_provided_by_DC
Contractor 1's net earnings per MWh supplied to grid (considering annual Inv. and O&M cost): -3.9 EUR/MWh_supplied_to_grid
Contractor 2's net earnings per MWh of heat supplied: 0.5 EUR/MWh_provided_by_DC
IRR
BREAK-
EVEN
Contractor 1 / DH operator: Internal rate of return: 1.98 % (considering calculatory life time of 15 years)
Contractor 2 / DC operator: Internal rate of return: 6.83 % (considering calculatory life time of 15 years)
Break-even price for waste heat supplied by DC: -3.17 EUR/MWh_provided_by_DH
Break-even price for waste heat supplied by DC: 1.52 EUR/MWh_provided_by_DC
Break-even price for waste heat utilised by HP: 1.61 EUR/MWh_utilized_by_HP
Break-even price for waste heat utilised by HP: -3.36 EUR/MWh_utilised_by_HP
Break-even price for waste heat fed into DH grid: -2.4 EUR/MWh_fed_into_grid
OUTPUT
Actor
Contractor 1's investments (incl. subsidies, excl. cost share of heat recovery): 4815 kEUR (lump-sum)
Contractor 1's annual operation independent expenses (excl. cost share of heat recovery): 348.5 kEUR/yr
Contractor 1's annual variable costs (excl. cost share of heat recovery): 615 kEUR/yr
Shares are to be defined in sheet >Main Results - IRR DC Operator<
B1
B2
B3
B1
B2
B3
Contractor 2 / Data centre operator
Waste heat recovery system
Contractor 1 / District heating operator: heat utilisation
District heating operator

## Calculation Break-Even
Go to Content
Summary of Results
Contractor 1 / DH operator | CAPEX: Investment & planning & one-time costs (HP and Booster) | 5065000 | EUR | 487973.6867 | EUR/yr | 21.3086 | EUR/MWh_fed_into_grid
| CAPEX: Piping and grid connection costs | 1550000 | EUR | 149330.5458 | EUR/yr | 6.5209 | EUR/MWh_fed_into_grid
| CAPEX: Decommission costs (HP and Booster, etc.) | 0 | EUR | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| CAPEX: Residual value (HP and Booster) | 0 | EUR | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| CAPEX: One-time subsidies (HP and Booster) (Earnings) | -1800000 | EUR | -173416.1177 | EUR/yr | -7.5727 | EUR/MWh_fed_into_grid
| CAPEX: Waste Heat Recovery System paid for by Contractor 1 / DH operator | 0 | EUR | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| CAPEX (total, incl. lump-sum subsidies) | 4815000 | EUR | 463888.1148 | EUR/yr | 20.2569 | EUR/MWh_fed_into_grid
| CAPEX (total, incl. lump-sum subsidies excl. heat extraction system investment costs share paid by contractor 1) | 4815000 | EUR | 463888.1148 | EUR/yr | 20.2569 | EUR/MWh_fed_into_grid
| OPEX - fix: Waste heat payment to Contractor 2 / DC operator under a take-or-pay contract (based on the negotiated price p_0) |  |  | 34767.5272 | EUR/yr | 1.5182 | EUR/MWh_fed_into_grid
| OPEX - fix: Regular annual costs (HP and Booster) |  |  | 68000 | EUR/yr | 2.9694 | EUR/MWh_fed_into_grid
| OPEX - fix: Personnel |  |  | 20000 | EUR/yr | 0.87335 | EUR/MWh_fed_into_grid
| OPEX - fix: Rent |  |  | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| OPEX - fix: Capacity dependent annual subsidies (HP and Booster) ( Earnings) |  |  | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| OPEX - fix: Consumption independent grid fee costs HP & Booster |  |  | 225757.5758 | EUR/yr | 9.8583 | EUR/MWh_fed_into_grid
| OPEX - fix: Waste Heat Recovery System paid for by Contractor 1 / DH operator |  |  | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| OPEX - fix (total) excl. waste heat payment to Contractor 2 / DC operator |  |  | 313757.5758 | EUR/yr | 13.701 | EUR/MWh_fed_into_grid
| OPEX - fix (total) incl. waste heat payment to Contractor 2 / DC operator |  |  | 348525.103 | EUR/yr | 15.2193 | EUR/MWh_fed_into_grid
| OPEX - fix (total) excl. waste heat payment to Contractor 2 / DC Operator (take-or-pay) excluding heat extraction system investment costs share paid by contractor 1 |  |  | 313757.5758 | EUR/yr | 13.701 | EUR/MWh_fed_into_grid
| OPEX - fix (total) incl. waste heat payment to Contractor 2 / DC Operator (take-or-pay) excluding heat extraction system investment costs share paid by contractor 1 |  |  | 348525.103 | EUR/yr | 15.2193 | EUR/MWh_fed_into_grid
| OPEX - var: Waste heat payment to Contractor 2 / DC Operator under a pay-as-you-go contract (based on the negotiated price p_1) |  |  | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| OPEX - var: Electricity costs (HP) |  |  | 571161.0435 | EUR/yr | 24.9412 | EUR/MWh_fed_into_grid
| OPEX - var: Fuel costs (Booster) |  |  | 3674.4668 | EUR/yr | 0.16046 | EUR/MWh_fed_into_grid
| OPEX - var: Electricity costs (Auxiliary) |  |  | 40207.4188 | EUR/yr | 1.7558 | EUR/MWh_fed_into_grid
| OPEX - var: O&M Var (w.o. electricity for heat pump and electricity / fuel for booster) |  |  | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| OPEX - var: Waste heat dependent annual subsidies (HP and Booster) (Earnings) |  |  | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| OPEX - var: Waste Heat Recovery System paid for by Contractor 1 / DH Operator |  |  | 0 | EUR/yr | 0 | EUR/MWh_fed_into_grid
| OPEX - var (total) excl. waste heat payment to Contractor 2 / DC operator |  |  | 615042.9291 | EUR/yr | 26.8575 | EUR/MWh_fed_into_grid
| OPEX - var (total) incl. waste heat payment to Contractor 2 / DC operator (pay-as-you-go) |  |  | 615042.9291 | EUR/yr | 26.8575 | EUR/MWh_fed_into_grid
| OPEX - var (total) excl. waste heat payment to Contractor 2 / DC operator (pay-as-you-go) excluding heat extraction system investment costs share paid by contractor 1 |  |  | 615042.9291 | EUR/yr | 26.8575 | EUR/MWh_fed_into_grid
| OPEX - var (total) incl. waste heat payment to Contractor 2 / DC operator (pay-as-you-go) excluding heat extraction system investment costs share paid by contractor 1 |  |  | 615042.9291 | EUR/yr | 26.8575 | EUR/MWh_fed_into_grid
| Earnings - Avoided variable costs (SRMC) of alternative production (i.e. refrence marginal heat costs) |  |  | 1337630.8197 | EUR/yr | 58.4112 | EUR/MWh_fed_into_grid
| Expenses / LCOH without payment to Contractor 2 / DC operator |  |  | 1392688.6197 | EUR/yr | 60.8154 | EUR/MWh_fed_into_grid
| Expenses - Payment to Contractor 2 / DC operator |  |  | 34767.5272 | EUR/yr | 1.5182 | EUR/MWh_fed_into_grid
| Expenses / LCOH without payment to Contractor 2 / DC operator excluding heat extraction system investment costs share paid by contractor 1 |  |  | 1392688.6197 | EUR/yr | 60.8154 | EUR/MWh_fed_into_grid
| Total net earnings of Contractor 1 / DH operator |  |  |  |  | -5.1672 | EUR/MWh_supplied_by_DC
| Total net earnings of Contractor 1 / DH operator |  |  |  |  | -5.4835 | EUR/MWh_waste_heat_utilized_by_HP
| Total net earnings of Contractor 1 / DH operator |  |  | -89825.3272 | EUR/yr | -3.9225 | EUR/MWh_fed_into_grid
| Net earnings of contractor 1 / DH operator excluding heat extraction system investment costs share paid by contractor 1 |  |  | -89825.3272 | EUR/yr | -3.9225 | EUR/MWh_fed_into_grid
Contractor 2 / DC Operator | CAPEX: Investments heat recovery & planning & heat exchanger, etc., paid for by DC operator | 550080 | EUR | 52995.9656 | EUR/yr | 3.0486 | EUR/MWh_provided_by_DC
| CAPEX: Piping, paid for by DC operator | 126000 | EUR | 12139.1282 | EUR/yr | 0.6983 | EUR/MWh_provided_by_DC
| CAPEX: One-time subsidies (Earnings), received by DC Operator | 0 | EUR | 0 | EUR/yr | 0 | EUR/MWh_provided_by_DC
| CAPEX (total, incl. lump-sum subsidies) | 676080 | EUR | 65135.0938 | EUR/yr | 3.7469 | EUR/MWh_provided_by_DC
| OPEX - fix: Other operation independent O&M costs, paid for by DC operator |  |  | 50000 | EUR/yr | 2.8762 | EUR/MWh_provided_by_DC
| OPEX - fix: Energy costs under p_0 paid to external entity |  |  | 0 | EUR/yr | 0 | EUR/MWh_provided_by_DC
| OPEX - (total) fixed costs |  |  | 50000 | EUR/yr | 2.8762 | EUR/MWh_provided_by_DC
| OPEX - var: O&M costs paid by DC operator |  |  | 32761.8431 | EUR/yr | 1.8846 | EUR/MWh_provided_by_DC
| OPEX - (total) variable costs |  |  | 32761.8431 | EUR/yr | 1.8846 | EUR/MWh_provided_by_DC
| Earnings: Payment from Contractor 1 / DH operator (take-or-pay OR pay-as-you-go) |  |  | 34767.5272 | EUR/yr | 2 | EUR/MWh_provided_by_DC
| Earnings: Avoided electricity costs for cooling |  |  | 121445.7164 | EUR/yr | 6.9862 | EUR/MWh_provided_by_DC
| Total expenses |  |  | 147896.9369 | EUR/yr | 8.5078 | EUR/MWh_provided_by_DC
| Total net earnings of Contractor 2 / DC operator |  |  | 8316.3068 | EUR/yr | 0.4784 | EUR/MWh_provided_by_DC
| Produced heat - fed into grid | 458005.2705 | MWh for entire project lifetime | 22900.2635 | MWh/yr
| Waste heat utilised in heat pump | 327618.4308 | MWh for entire project lifetime | 16380.9215 | MWh/yr
| Waste heat provided by DC | 347675.2722 | MWh for entire project lifetime | 17383.7636 | MWh/yr
| Reference avoided marginal heat costs |  |  | 1337630.8197 | EUR/yr | 58.4112 | EUR/MWh_fed_into_grid
| LCOH - excl. payment to DC operator based on negotiated price p_1 between Contractor 1 and Contractor 2 |  |  |  |  | 60.8154 | EUR/MWh_fed_into_grid | Link to additional information / German translation
| LCOH - incl. payment to DC operator based on negotiated price p_1 between Contractor 1 and Contractor 2 |  |  |  |  | 62.3336 | EUR/MWh_fed_into_grid | Link to additional information / German translation
| LCOH - excl. payment to DC operator based on negotiated price p_1 between Contractor 1 and Contractor 2 excluding heat extraction system investment costs share paid by contractor 1 |  |  |  |  | 60.8154 | EUR/MWh_fed_into_grid | Link to additional information / German translation
| LCOH - incl. payment to DC operator based on negotiated price p_1 between Contractor 1 and Contractor 2 excluding heat extraction system investment costs share paid by contractor 1 |  |  |  |  | 62.3336 | EUR/MWh_fed_into_grid | Link to additional information / German translation
The calculated break-even price for waste heat is the upper limit the DH operator can afford to pay for the waste heat to reach the break-even point under the pre-defined economic parameters (Expected IRR and calculatory life time as defined in the Project Sheet)
| Contractor 1: Break-even waste heat price per MWh fed into the grid |  |  |  |  | -2.4042 | EUR/MWh_fed_into_grid
| Contractor 1: Break-even waste heat price per MWh waste heat utilised in heat pump |  |  |  |  | -3.3611 | EUR/MWh_utilized_by_HP
| Contractor 1: Break-even waste heat price per MWh waste heat provided by DC operator |  |  |  |  | -3.1672 | EUR/MWh_provided_by_DC
| Contractor 1: Break-even waste heat price per MWh waste heat utilised in heat pump excluding heat extraction system investment costs share paid by contractor 1 |  |  |  |  | -3.3611 | EUR/MWh_utilized_by_HP
| Contractor 1: Break-even waste heat price per MWh waste heat provided by DC operator excluding heat extraction system investment costs share paid by contractor 1 |  |  |  |  | -3.1672 | EUR/MWh_provided_by_DC
| The calculated break-even price for waste heat is the lower limit for the DC operator to receive to reach the break-even point under the predefined economic parameters. (Expected IRR and calculatory life time as defined in the Project Sheet) | [6 empty] | Link to additional information / German translation
| Contractor 2 / DC operator: Break-even waste heat price per MWh waste heat utilised in heat pump |  |  |  |  | 1.6148 | EUR/MWh_utilized_by_HP | Link to additional information / German translation
| Contractor 2 / DC operator: Break-even waste heat price per MWh waste heat provided by DC operator |  |  |  |  | 1.5216 | EUR/MWh_provided_by_DC
Underlying assumptions on waste heat contract (used to determine SRMC)
| Share Take-or-pay (ToP) Contract: In case of ToP contract, the waste heat price is not part of the SRMC, but constitutes annual fix costs |  |  |  |  | 100%
| Share pay-as-you-go (payg) Contract: In case of payg contract, the waste heat price is part of the SRMC, and has an impact on SRMC |  |  |  |  | 0%
| Average waste heat price (p_1 as negotiated between Contractor 1 and Contractor 2) per heat fed into grid |  |  |  |  | 1.5182 | EUR/MWh_fed_into_grid
| Average waste heat price (p_1 as negotiated between Contractor 1 and Contractor 2) per waste heat utilized by Contractor 1 |  |  |  |  | 2.1224 | EUR/MWh_utilized_by_HP
| Average waste heat price (p_1 as negotiated between Contractor 1 and Contractor 2) per waste heat provided by DC operator |  |  |  |  | 2 | EUR/MWh_provided_by_DC
Go to Additional Summary of Cost Structure

## Operation at Typical Day
Go to Content Sheet
Colour Code | Header
Item / unit
User input
Cell with formula
Go to content
Input - not used for calculation
| Control cells |  |  |  | Control cells
Check settings / input data, there might be some error
|  | Select typical day | 3
Spring / fall weekend
|  | Hour of the day | Waste heat output DC | Max heat demand grid | Heat fed into grid considering actual operation | Waste heat input from DC actual operation | Electricity input for heat pump actual operation | Energy input for booster actual operation
|  |  | MW_th | MW_th | MW_th | MW_th | MW_th | MW_th
|  | 1 | 2 | 6 | 2.8605 | 2 | 0.88942 | 0
|  | 2 | 2 | 6 | 2.8605 | 2 | 0.88942 | 0
|  | 3 | 2 | 6 | 2.8605 | 2 | 0.88942 | 0
|  | 4 | 2 | 6 | 2.8778 | 2 | 0.90689 | 0
|  | 5 | 2 | 6 | 2.8958 | 2 | 0.92507 | 0
|  | 6 | 2 | 6 | 2.8778 | 2 | 0.90689 | 0
|  | 7 | 2 | 6 | 2.8778 | 2 | 0.90689 | 0
|  | 8 | 2 | 6 | 2.8605 | 2 | 0.88942 | 0
|  | 9 | 2 | 6 | 2.8439 | 2 | 0.8726 | 0
|  | 10 | 2 | 6 | 2.8278 | 2 | 0.85641 | 0
|  | 11 | 2 | 6 | 2.8124 | 2 | 0.84081 | 0
|  | 12 | 2 | 6 | 2.7975 | 2 | 0.82576 | 0
|  | 13 | 2 | 6 | 2.7831 | 2 | 0.81125 | 0
|  | 14 | 2 | 6 | 2.7693 | 2 | 0.79724 | 0
|  | 15 | 2 | 6 | 2.7693 | 2 | 0.79724 | 0
|  | 16 | 2 | 6 | 2.7559 | 2 | 0.7837 | 0
|  | 17 | 2 | 6 | 2.7693 | 2 | 0.79724 | 0
|  | 18 | 2 | 6 | 2.7831 | 2 | 0.81125 | 0
|  | 19 | 2 | 6 | 2.7975 | 2 | 0.82576 | 0
|  | 20 | 2 | 6 | 2.8124 | 2 | 0.84081 | 0
|  | 21 | 2 | 6 | 2.8278 | 2 | 0.85641 | 0
|  | 22 | 2 | 6 | 2.8439 | 2 | 0.8726 | 0
|  | 23 | 2 | 6 | 2.8439 | 2 | 0.8726 | 0
|  | 24 | 2 | 6 | 2.8605 | 2 | 0.88942 | 0
Spring / fall weekend
|  | Hour of the day | Electricity price Heat pump | Fuel price booster | SRMC Waste heat price (if Pay-as-you-go contract) | SRMC of heat production from waste heat | SRMC of alternative heat production | Heat pump is running
|  |  | EUR/MWh | EUR/MWh | EUR/MWh | MW_th | MW_th
|  | 1 | 92.85 | 92.85 | 0 | 30.304 | 60 | 1
|  | 2 | 81.59 | 81.59 | 0 | 26.8029 | 60 | 1
|  | 3 | 80.53 | 80.53 | 0 | 26.4734 | 60 | 1
|  | 4 | 75.4 | 75.4 | 0 | 25.1952 | 60 | 1
|  | 5 | 74.88 | 74.88 | 0 | 25.3548 | 60 | 1
|  | 6 | 74.62 | 74.62 | 0 | 24.9494 | 60 | 1
|  | 7 | 75.43 | 75.43 | 0 | 25.2047 | 60 | 1
|  | 8 | 71.53 | 71.53 | 0 | 23.675 | 60 | 1
|  | 9 | 71.88 | 71.88 | 0 | 23.4896 | 60 | 1
|  | 10 | 66.38 | 66.38 | 0 | 21.5374 | 60 | 1
|  | 11 | 43.99 | 43.99 | 0 | 14.5858 | 60 | 1
|  | 12 | 47.96 | 47.96 | 0 | 15.5911 | 60 | 1
|  | 13 | 17.06 | 17.06 | 0 | 6.4071 | 60 | 1
|  | 14 | 11.28 | 11.28 | 0 | 4.6817 | 60 | 1
|  | 15 | 10.1 | 10.1 | 0 | 4.342 | 60 | 1
|  | 16 | 11.75 | 11.75 | 0 | 4.7758 | 60 | 1
|  | 17 | 17.01 | 17.01 | 0 | 6.3313 | 60 | 1
|  | 18 | 69.22 | 69.22 | 0 | 21.6111 | 60 | 1
|  | 19 | 85.6 | 85.6 | 0 | 26.7016 | 60 | 1
|  | 20 | 100.36 | 100.36 | 0 | 31.4384 | 60 | 1
|  | 21 | 106.26 | 106.26 | 0 | 33.615 | 60 | 1
|  | 22 | 102.07 | 102.07 | 0 | 32.753 | 60 | 1
|  | 23 | 100.41 | 100.41 | 0 | 32.2437 | 60 | 1
|  | 24 | 99.46 | 99.46 | 0 | 32.3592 | 60 | 1
Spring / fall weekend
|  | Hour of the day | Flow temperature of data centre cooling system | Flow Temperature HP | DH supply line temperature | Required temperature sink out | DH return line temperature | Temperature heat pump sink in | COP under current conditions
|  |  | °C | °C | °C | °C | °C | °C
|  | 1 | 40 | 37 | 86.6667 | 89.6667 | 45 | 48 | 3.2487
|  | 2 | 40 | 37 | 86.6667 | 89.6667 | 45 | 48 | 3.2487
|  | 3 | 40 | 37 | 86.6667 | 89.6667 | 45 | 48 | 3.2487
|  | 4 | 40 | 37 | 88.3333 | 91.3333 | 45 | 48 | 3.2053
|  | 5 | 40 | 37 | 90 | 93 | 45 | 48 | 3.162
|  | 6 | 40 | 37 | 88.3333 | 91.3333 | 45 | 48 | 3.2053
|  | 7 | 40 | 37 | 88.3333 | 91.3333 | 45 | 48 | 3.2053
|  | 8 | 40 | 37 | 86.6667 | 89.6667 | 45 | 48 | 3.2487
|  | 9 | 40 | 37 | 85 | 88 | 45 | 48 | 3.292
|  | 10 | 40 | 37 | 83.3333 | 86.3333 | 45 | 48 | 3.3353
|  | 11 | 40 | 37 | 81.6667 | 84.6667 | 45 | 48 | 3.3787
|  | 12 | 40 | 37 | 80 | 83 | 45 | 48 | 3.422
|  | 13 | 40 | 37 | 78.3333 | 81.3333 | 45 | 48 | 3.4653
|  | 14 | 40 | 37 | 76.6667 | 79.6667 | 45 | 48 | 3.5087
|  | 15 | 40 | 37 | 76.6667 | 79.6667 | 45 | 48 | 3.5087
|  | 16 | 40 | 37 | 75 | 78 | 45 | 48 | 3.552
|  | 17 | 40 | 37 | 76.6667 | 79.6667 | 45 | 48 | 3.5087
|  | 18 | 40 | 37 | 78.3333 | 81.3333 | 45 | 48 | 3.4653
|  | 19 | 40 | 37 | 80 | 83 | 45 | 48 | 3.422
|  | 20 | 40 | 37 | 81.6667 | 84.6667 | 45 | 48 | 3.3787
|  | 21 | 40 | 37 | 83.3333 | 86.3333 | 45 | 48 | 3.3353
|  | 22 | 40 | 37 | 85 | 88 | 45 | 48 | 3.292
|  | 23 | 40 | 37 | 85 | 88 | 45 | 48 | 3.292
|  | 24 | 40 | 37 | 86.6667 | 89.6667 | 45 | 48 | 3.2487

## Calculation of Typical Day
Go to Content
Colour Code | Header
Item / unit
User input
Cell with formula
Go to Content
Input - not used for calculation
Not used anymore: relevant for future works - do not change
Control cells
Check settings / input data, there might be some error
Typical Day ID | Name of typical day | Hour |  |  |  |  | Available waste heat (DC heat source) | Flow temperature of data centre cooling system | Flow Temperature HP | Return temperature HP / Flow temperature DC | Max heat demand - grid (HP heat sink) | DH supply line temperature | Delta T DH / Heat pump | Required temperature sink out | DH return line temperature | Temperature heat pump sink in | Actual Heat pump Temperature Sink Out | Nominal COP | COP increase due to higher heat source temperature | COP increase due to lower heat sink out temperature (eg. DH supply line temperature) | COP increase due to higher heat sink in temperature (eg. DH return line temperature) | COP at current operation conditions | Nominal capacity of heat pump | Reduced capacity of heat pump due to volume restrictions | Potential heat output - HP, including heat losses, not considering | HP output due to Booster Capacity restrictions | Delta T Booster | Required Booster heat output | Booster heat output | Total heat output before additional losses | Heat losses after HP | Total heat output after additional losses | Total heat output after considering restriction imposed by heat demand | Share of heat provided by heat pump and booster utilized by grid | Waste heat input from DC | Electricity input for heat pump | Energy input for booster | Avoided electricity demand due to reduced active cooling | Remaining electricity demand for active cooling | Waste heat price p_0 that is paid at the border between data centre cooling and waste heat recovery system under Take-or-Pay conditions | Energy costs p_0 for waste heat from DC | Variable O&M costs for heat recovery system operator | Total Hourly costs of heat recovery system operator | Negotiated Waste heat price p_1 | Contract type for waste heat between Contractor 1 / DH operator and Contractor 2 / data centre operator | Energy costs p_1 for waste heat from DC as provided by DC (take-or-pay) (Contractor 1) | Energy costs p_1 for waste heat from DC as taken (Pay-as-you-go) (Contractor 1) | Electricity price Heat pump | Fuel price booster | Electricity price auxiliary energy | Data centre operator: Electricity price for cooling unit | Data centre operator: Share of active cooling needed if heat is not taken up by DH | Average Subsidies given Contractor 1 per utilized waste heat | Electricity costs for heat pump (Contractor 1) | Electricity costs auxiliary energy (Contractor 1) | Fuel costs for booster (Contractor 1) | Avoided electricity costs due to reduced active cooling | Remaining electricity costs for active cooling | Subsidies given per utilized waste heat to Contractor 1 / DH Operator | Subsidies given per utilized waste heat to Contractor 1 / DH Operator considering that they must not exceed costs for electricity | Total energy costs considering subsidies Contractor 1 / DH operator including subsidies S3 provided for the utilized waste heat | Total energy costs per delivered Heat to Grid Contractor 1 / DH Operator | Total SRMC energy costs Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Variable (MWh-specific) O&M Costs Heat pump Contractor 1 / DH Operator | Variable (MWh-specific) O&M Costs Booster Contractor 1 / DH Operator | Total Hourly costs of Contractor 1 / DH Operator including subsidies S3 provided for the utilized waste heat | Short run marginal costs per hour Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator including subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator used to compare against reference SRMC alternative production | Reference SRMC alternative production [EUR/MWh_delivered] | Is Heat production because SRMC lower than alternative, temperature can be met and system is available | Operation hours | Operation hours in full-load-hours equivalents | Reference SRMC alternative production [EUR/h] | Typical Day ID | Hour | Name of typical day | Waste heat output DC | Max heat demand grid | Heat fed into grid considering actual operation | Waste heat input from DC actual operation | Electricity input for heat pump actual operation | Energy input for booster actual operation | SRMC Heat-pump is lower than SRMC of alternative heat production | Heat demand (DH) is given | Waste heat is available | Temperature demand of DH grid is met | Heat pump is running | Booster is running
[7 empty] | MW_th/hour | °C | °C | °C | MW | °C | °C | °C | °C | °C | °C | [5 empty] | MW_th | MW_th | MW_th | MW_th | °C | MW_th | MW_th | MW_th | MW_th | MW_th | MW_th | % | MW_th | MW_el | MW | MWh_el/hour | MWh_el/hour | EUR/MWh | EUR/hour | EUR/hour | EUR/hour | EUR/MWh |  | EUR/hour | EUR/hour | EUR/MWh | EUR/MWh | EUR/MWh | EUR/MWh | EUR/MWh | EUR/MWh | EUR/hour | EUR/hour | EUR/hour | EUR/hour | EUR/hour | EUR/hour | EUR/hour | EUR/hour | EUR/MWh_delivered | EUR/hour | EUR/hour | EUR/hour | EUR/hour | EUR/hour | EUR/MWh_delivered | EUR/MWh_delivered | EUR/MWh_delivered | EUR/MWh_delivered | True/False | hours | hours | EUR/h |  |  |  | MW_th | MW_th | MW_th | MW_th | MW_th | MW_th | True/False | True/False | True/False | True/False | True/False
Typical Day ID |  | Hour | Look-up row in Definition of typical day sheet | Look-up column in Definition of typical day sheet | Check reference hours (rows) | Check reference typical day (columns) | The thermal energy available from the data centre for recovery | Flow Temperature of the cooling system of the DC | Flow Temperature HP equals the temperature of the cooling system reduced by delta T of the heat exchanger | Return temperature HP / Flow temperature DC | The maximum heat that the district heating grid can accept per hour (Heat sink) | The required supply temperature for the district heating grid. | Temperature difference between HP and DH due to heat exchanger losses. | Temperature required by the DH grid and needs to be provided by Heatpump + booster (may be higher than what HP alone can deliver). | The return temperature of the district heating network. | Inlet temperature into the heat pump from the sink (DH side). | Temperature that needs to be delivered by heat pump. Restricted by either the upper limit of the heat pump or the grid supply line temperature | COP at nominal working conditions | Efficiency gain from lower DH supply temp. | Efficiency gain from lower DH supply temp.If negative value, than COP decrease | Efficiency gains from warmer DH return temp. | Real-time COP based on actual temperatures. | Max thermal output of the HP at nominal conditions. | Reduction of HP capacity due to lower than nominal temperature spread, eg. triggered by volume flow restrictions | Potential heat output of heat pump, not yet considering heat losses or restrictions of heat demand in grid | This considers heat pump output restrictions due to the limited booster capacity. Otherwise the heat cannot be delivered at the required temperature level | The temperature difference that needs to be delivered by the booster | The required booster output NOT considering the booster capacity limitation. | The actual booster output considering the installed booster capacity | Sum of HP and booster outputs (without considering heat losses and limitations due imposed by grid demand) | Heat Loss in pipes and heat exchangers | Sum of HP and booster outputs considering heat losses but NOT considering the limitations imposed by grid demand | Sum of HP and booster outputs considering heat losses and the limitations imposed by grid demand | The percentage of the total thermal energy output (from both the heat pump and the booster) that is actually delivered to and used by the district heating grid. | Waste heat from DC that is actually used. | Electrical energy used by the HP. | Fuel or electricity used by the booster. | Total hourly AVOIDED electricity due to less active cooling needs. (THIS ARE SAVINGS) | Total hourly remaining electricity demand for active cooling | This is the price the contractor needs to pay for the waste heat that is running the waste heat recovery system | Fixed energy cost under Take-or-Pay. In this case, waste heat costs are NOT part of SRMC | Usage-based maintenance and operational costs of heat recovery system | The total operational cost per hour incurred by the operator of the heat recovery system | This is the negotiated waste heat price p_1 between Contractor 1 / DH operator and Contractor 2 / data centre operator | Contract type defined in Project Sheet: (1) Take-or-pay contract or (2) Pay-as-you-go (utilized heat) | If Take-or-pay contract, then waste heat costs are NOT part of SRMC. These are costs for Contractor 1 / DH Operator and earnings for Contractor 2 / DC Operator | If Pay-as-you-go contract, then waste heat costs are part of SRMC. These are costs for Contractor 1 / DH Operator and earnings for Contractor 2 / DC Operator | Hourly electricity price used to calculate the operating cost of the heat pump. This price constitutes from the electricity price as defined in the sheet >Definition of Typical Day< plus the constant grid fee costs, as defined in the sheet >Project Setting< | Unit price of the energy carrier (e.g. gas, electricity) used by the booster for raising temperatures. | Unit price of electricity used for auxiliary components (e.g. pumps, control units). | Unit price of electricity used for auxiliary components (e.g. pumps, control units). | This is the share of required active cooling (as opposed to free cooling) that is required by the data centre operator if heat is not taken up by the DH network (Contractor 1) | Average financial incentive received per MWh of waste heat recovered and used by Contractor 1 (DH operator). | Total hourly electricity cost for operating the heat pump, based on consumption and price. | Total hourly cost for auxiliary systems using electricity (e.g., control systems, water pumps). | Total hourly cost of fuel used by the booster unit to provide additional heating. | Total hourly REDUCED electricity costs due to less active cooling needs. (THIS ARE SAVINGS) | Total hourly remaining electricity costs for active cooling | Hourly amount of subsidy received based on the actual volume of utilized waste heat - NOT CONSIDERING that they must not exceed electricity costs | Hourly amount of subsidy received based on the actual volume of utilized waste heat. | Total hourly energy costs after subtracting any received subsidies. | Energy costs per MWh of heat actually fed into the district heating grid (excluding O&M). | If take-or-pay contract, then the energy costs for waste heat are not SRMC but fix costs, ALSO subsidies are not considered as SRMC (even if they are) | Hourly share of operational and maintenance costs for the heat pump. | Operational and maintenance costs for the booster | Sum of all variable costs per hour, including energy and O&M for the heat pump and booster. | Total variable costs (SRMC) including O&M costs , BE AWARE THAT subsidies are not considered as SRMC (even if they are) | Total variable costs (SRMC) including O&M costs excluding the S3 subsidies provided for utilizing waste heat | Total variable costs (SRMC) including O&M costs including the S3 subsidies provided for utilizing waste heat | These are the Variable costs that are used compare against the reference SRMC of alternative production source | The cost of producing 1 MWh of heat delivered to heat network using alternative sources that the recovered data centre heat replaces. |  | 1 if system is running | Actual heat output from heat pump / nominal capacity of the heat pump | The hourly cost of producing 1 MWh of heat delivered using alternative sources that the recovered data centre heat replaces. |  |  |  | The total thermal energy available as waste heat from the data centre, before any recovery or use. | The upper limit for heat that the district heating grid can accept at a given hour. | Total heat production considering whether or not system is running | Total utilized waste heat considering whether or not system is running | Total electricity demand for heat pump considering whether or not system is running | Total fuel demand booster considering whether or not system is running | True/False | True/False | True/False | True/False | True/False | True/False
| 14 | [5 empty] | 1 | 3 | 3 | 28 | 2 | 4 | 3 | 4 | 5 | 5 | 95 | 3 | 0.02 | 0.026 | 0 |  | MW_th: 3; MW_th: 30; MW_th: 0.5; MW_th: 1; MW: 99 | 7.5 | 7.5 | 0 |  | 2 | [5 empty] | 7 | 8 | 27 | 9 | 10 | 0 |  | 2 | [8 empty] | 0 | 0 |  |  |  |  | 0 | 6 | [6 empty] | 14
[19 empty] | 25 | 90 | 60 |  | MW_th: 0.5 | [10 empty] | 11 | 11 |  | 11
0.19
Typical Day ID | Name of typical day | Hour |  |  |  |  | Available waste heat (DC heat source) | Flow temperature of data centre cooling system | Flow Temperature HP | Return temperature HP / Flow temperature DC | Max heat demand - grid (HP heat sink) | DH supply line temperature | Delta T DH / Heat pump | Required temperature sink out | DH return line temperature | Temperature heat pump sink in | Actual Heat pump Temperature Sink Out | Nominal COP | COP increase due to higher heat source temperature | COP increase due to lower heat sink out temperature (eg. DH supply line temperature) | COP increase due to higher heat sink in temperature (eg. DH return line temperature) | COP at current operation conditions | Nominal capacity of heat pump | Reduced capacity of heat pump due to volume restrictions | Potential heat output - HP, including heat losses, not considering | HP output due to Booster Capacity restrictions | Delta T Booster | Required Booster heat output | Booster heat output | Total heat output before additional losses | Heat losses after HP | Total heat output after additional losses | Total heat output after considering restriction imposed by heat demand | Share of heat provided by heat pump and booster utilized by grid | Waste heat input from DC | Electricity input for heat pump | Energy input for booster | Avoided electricity demand due to reduced active cooling | Remaining electricity demand for active cooling | Waste heat price p_0 that is paid at the border between data centre cooling and waste heat recovery system under Take-or-Pay conditions | Energy costs p_0 for waste heat from DC | Variable O&M costs for heat recovery system operator | Total Hourly costs of heat recovery system operator | Negotiated Waste heat price p_1 | Contract type for waste heat between Contractor 1 / DH operator and Contractor 2 / data centre operator | Energy costs p_1 for waste heat from DC as provided by DC (take-or-pay) (Contractor 1) | Energy costs p_1 for waste heat from DC as taken (Pay-as-you-go) (Contractor 1) | Electricity price Heat pump | Fuel price booster | Electricity price auxiliary energy | Data centre operator: Electricity price for cooling unit | Data centre operator: Share of active cooling needed if heat is not taken up by DH | Average Subsidies given Contractor 1 per utilized waste heat | Electricity costs for heat pump (Contractor 1) | Electricity costs auxiliary energy (Contractor 1) | Fuel costs for booster (Contractor 1) | Avoided electricity costs due to reduced active cooling | Remaining electricity costs for active cooling | Subsidies given per utilized waste heat to Contractor 1 / DH Operator | Subsidies given per utilized waste heat to Contractor 1 / DH Operator considering that they must not exceed costs for electricity | Total energy costs considering subsidies Contractor 1 / DH operator including subsidies S3 provided for the utilized waste heat | Total energy costs per delivered Heat to Grid Contractor 1 / DH Operator | Total SRMC energy costs Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Variable (MWh-specific) O&M Costs Heat pump Contractor 1 / DH Operator | Variable (MWh-specific) O&M Costs Booster Contractor 1 / DH Operator | Total Hourly costs of Contractor 1 / DH Operator including subsidies S3 provided for the utilized waste heat | Short run marginal costs per hour Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator including subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator used to compare against reference SRMC alternative production | Reference SRMC alternative production [EUR/MWh_delivered] | Is Heat production because SRMC lower than alternative, temperature can be met and system is available | Operation hours | Operation hours in full-load-hours equivalents | Reference SRMC alternative production [EUR/h] | Typical Day ID | Hour | Name of typical day | Waste heat output DC | Max heat demand grid | Heat fed into grid considering actual operation | Waste heat input from DC actual operation | Electricity input for heat pump actual operation | Energy input for booster actual operation | SRMC Heat-pump is lower than SRMC of alternative heat production | Heat demand (DH) is given | Waste heat is available | Temperature demand of DH grid is met | Heat pump is running | Booster is running
1 | Winter day | 1 | 35 | 5 | 1 | 1 | 2 | 40 | 37 | 28 | 6 | 77 | 3 | 80 | 45 | 48 | 80 | 3 | 0.24 | 0.26 | 0 | 3.5 | 3 | 3 | 2.8 | 2.8 | 0 | 0 | 0 | 2.8 | 0.028 | 2.772 | 2.772 | 100% | 2 | 0.8 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 77 | 77 | 135 | 76 | 20% | 0 | 61.6 | 7.56 | 0 | 4.0533 | 0 | 0 | 0 | 73.16 | 26.3925 | 69.16 | 0 | 0 | 73.16 | 69.16 | 24.9495 | 24.9495 | 24.9495 | 65 | 1 | 1 | 0.93333 | 180.18 | 1 | 1 | Winter day | 2 | 6 | 2.772 | 2 | 0.8 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 2 | 36 | 5 | 2 | 1 | 2 | 40 | 37 | 28 | 6 | 77 | 3 | 80 | 45 | 48 | 80 | 3 | 0.24 | 0.26 | 0 | 3.5 | 3 | 3 | 2.8 | 2.8 | 0 | 0 | 0 | 2.8 | 0.028 | 2.772 | 2.772 | 100% | 2 | 0.8 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 74.45 | 74.45 | 135 | 73.45 | 20% | 0 | 59.56 | 7.56 | 0 | 3.9173 | 0 | 0 | 0 | 71.12 | 25.6566 | 67.12 | 0 | 0 | 71.12 | 67.12 | 24.2136 | 24.2136 | 24.2136 | 65 | 1 | 1 | 0.93333 | 180.18 | 1 | 2 | Winter day | 2 | 6 | 2.772 | 2 | 0.8 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 3 | 37 | 5 | 3 | 1 | 2 | 40 | 37 | 28 | 6 | 77 | 3 | 80 | 45 | 48 | 80 | 3 | 0.24 | 0.26 | 0 | 3.5 | 3 | 3 | 2.8 | 2.8 | 0 | 0 | 0 | 2.8 | 0.028 | 2.772 | 2.772 | 100% | 2 | 0.8 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 74.54 | 74.54 | 135 | 73.54 | 20% | 0 | 59.632 | 7.56 | 0 | 3.9221 | 0 | 0 | 0 | 71.192 | 25.6825 | 67.192 | 0 | 0 | 71.192 | 67.192 | 24.2395 | 24.2395 | 24.2395 | 65 | 1 | 1 | 0.93333 | 180.18 | 1 | 3 | Winter day | 2 | 6 | 2.772 | 2 | 0.8 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 4 | 38 | 5 | 4 | 1 | 2 | 40 | 37 | 28 | 6 | 79 | 3 | 82 | 45 | 48 | 82 | 3 | 0.24 | 0.208 | 0 | 3.448 | 3 | 3 | 2.817 | 2.817 | 0 | 0 | 0 | 2.817 | 0.02817 | 2.7888 | 2.7888 | 100% | 2 | 0.81699 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 72.82 | 72.82 | 135 | 71.82 | 20% | 0 | 59.4935 | 7.6059 | 0 | 3.8304 | 0 | 0 | 0 | 71.0993 | 25.4944 | 67.0993 | 0 | 0 | 71.0993 | 67.0993 | 24.0601 | 24.0601 | 24.0601 | 65 | 1 | 1 | 0.939 | 181.2735 | 1 | 4 | Winter day | 2 | 6 | 2.7888 | 2 | 0.81699 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 5 | 39 | 5 | 5 | 1 | 2 | 40 | 37 | 28 | 6 | 83 | 3 | 86 | 45 | 48 | 86 | 3 | 0.24 | 0.104 | 0 | 3.344 | 3 | 3 | 2.8532 | 2.8532 | 0 | 0 | 0 | 2.8532 | 0.028532 | 2.8247 | 2.8247 | 100% | 2 | 0.85324 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 72.85 | 72.85 | 135 | 71.85 | 20% | 0 | 62.1587 | 7.7038 | 0 | 3.832 | 0 | 0 | 0 | 73.8625 | 26.1487 | 69.8625 | 0 | 0 | 73.8625 | 69.8625 | 24.7326 | 24.7326 | 24.7326 | 65 | 1 | 1 | 0.95108 | 183.6061 | 1 | 5 | Winter day | 2 | 6 | 2.8247 | 2 | 0.85324 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 6 | 40 | 5 | 6 | 1 | 2 | 40 | 37 | 28 | 6 | 93 | 3 | 96 | 45 | 48 | 95 | 3 | 0.24 | -0.13 | 0 | 3.11 | 3 | 3 | 2.9479 | 2.9479 | 1 | 0.062721 | 0.062721 | 3.0106 | 0.030106 | 2.9805 | 2.9805 | 100% | 2 | 0.94787 | 0.063354 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 72.75 | 72.75 | 135 | 71.75 | 20% | 0 | 68.9573 | 8.1286 | 4.609 | 3.8267 | 0 | 0 | 0 | 85.6949 | 28.752 | 81.6949 | 0 | 0 | 85.6949 | 81.6949 | 27.41 | 27.41 | 27.41 | 65 | 1 | 1 | 0.98262 | 193.7313 | 1 | 6 | Winter day | 2 | 6 | 2.9805 | 2 | 0.94787 | 0.063354 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 1.01
1 | Winter day | 7 | 41 | 5 | 7 | 1 | 2 | 40 | 37 | 28 | 6 | 95 | 3 | 98 | 45 | 48 | 95 | 3 | 0.24 | -0.13 | 0 | 3.11 | 3 | 3 | 2.9479 | 2.9479 | 3 | 0.18816 | 0.18816 | 3.136 | 0.03136 | 3.1047 | 3.1047 | 100% | 2 | 0.94787 | 0.19006 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 73.59 | 73.59 | 135 | 72.59 | 20% | 0 | 69.7536 | 8.4673 | 13.9867 | 3.8715 | 0 | 0 | 0 | 96.2075 | 30.988 | 92.2075 | 0 | 0 | 96.2075 | 92.2075 | 29.6996 | 29.6996 | 29.6996 | 65 | 1 | 1 | 0.98262 | 201.8035 | 1 | 7 | Winter day | 2 | 6 | 3.1047 | 2 | 0.94787 | 0.19006 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 1.01
1 | Winter day | 8 | 42 | 5 | 8 | 1 | 2 | 40 | 37 | 28 | 6 | 95 | 3 | 98 | 45 | 48 | 95 | 3 | 0.24 | -0.13 | 0 | 3.11 | 3 | 3 | 2.9479 | 2.9479 | 3 | 0.18816 | 0.18816 | 3.136 | 0.03136 | 3.1047 | 3.1047 | 100% | 2 | 0.94787 | 0.19006 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 77.9 | 77.9 | 135 | 76.9 | 20% | 0 | 73.8389 | 8.4673 | 14.8059 | 4.1013 | 0 | 0 | 0 | 101.112 | 32.5677 | 97.112 | 0 | 0 | 101.112 | 97.112 | 31.2793 | 31.2793 | 31.2793 | 65 | 1 | 1 | 0.98262 | 201.8035 | 1 | 8 | Winter day | 2 | 6 | 3.1047 | 2 | 0.94787 | 0.19006 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 1.01
1 | Winter day | 9 | 43 | 5 | 9 | 1 | 2 | 40 | 37 | 28 | 6 | 93 | 3 | 96 | 45 | 48 | 95 | 3 | 0.24 | -0.13 | 0 | 3.11 | 3 | 3 | 2.9479 | 2.9479 | 1 | 0.062721 | 0.062721 | 3.0106 | 0.030106 | 2.9805 | 2.9805 | 100% | 2 | 0.94787 | 0.063354 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 85.82 | 85.82 | 135 | 84.82 | 20% | 0 | 81.346 | 8.1286 | 5.4371 | 4.5237 | 0 | 0 | 0 | 98.9116 | 33.1864 | 94.9116 | 0 | 0 | 98.9116 | 94.9116 | 31.8444 | 31.8444 | 31.8444 | 65 | 1 | 1 | 0.98262 | 193.7313 | 1 | 9 | Winter day | 2 | 6 | 2.9805 | 2 | 0.94787 | 0.063354 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 1.01
1 | Winter day | 10 | 44 | 5 | 10 | 1 | 2 | 40 | 37 | 28 | 6 | 92 | 3 | 95 | 45 | 48 | 95 | 3 | 0.24 | -0.13 | 0 | 3.11 | 3 | 3 | 2.9479 | 2.9479 | 0 | 0 | 0 | 2.9479 | 0.029479 | 2.9184 | 2.9184 | 100% | 2 | 0.94787 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 88.9 | 88.9 | 135 | 87.9 | 20% | 0 | 84.2654 | 7.9592 | 0 | 4.688 | 0 | 0 | 0 | 96.2246 | 32.9718 | 92.2246 | 0 | 0 | 96.2246 | 92.2246 | 31.6012 | 31.6012 | 31.6012 | 65 | 1 | 1 | 0.98262 | 189.6953 | 1 | 10 | Winter day | 2 | 6 | 2.9184 | 2 | 0.94787 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 11 | 45 | 5 | 11 | 1 | 2 | 40 | 37 | 28 | 6 | 88 | 3 | 91 | 45 | 48 | 91 | 3 | 0.24 | -0.026 | 0 | 3.214 | 3 | 3 | 2.9033 | 2.9033 | 0 | 0 | 0 | 2.9033 | 0.029033 | 2.8743 | 2.8743 | 100% | 2 | 0.90334 | 0 | 0.093333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 82.8 | 82.8 | 135 | 81.8 | 35% | 0 | 74.7967 | 7.839 | 0 | 7.6347 | 0 | 0 | 0 | 86.6358 | 30.1414 | 82.6358 | 0 | 0 | 86.6358 | 82.6358 | 28.7498 | 28.7498 | 28.7498 | 65 | 1 | 1 | 0.96778 | 186.8301 | 1 | 11 | Winter day | 2 | 6 | 2.8743 | 2 | 0.90334 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 12 | 46 | 5 | 12 | 1 | 2 | 40 | 37 | 28 | 6 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.24 | 0.182 | 0 | 3.422 | 3 | 3 | 2.8258 | 2.8258 | 0 | 0 | 0 | 2.8258 | 0.028258 | 2.7975 | 2.7975 | 100% | 2 | 0.82576 | 0 | 0.093333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 81.77 | 81.77 | 135 | 80.77 | 35% | 0 | 67.5227 | 7.6296 | 0 | 7.5385 | 0 | 0 | 0 | 79.1523 | 28.2939 | 75.1523 | 0 | 0 | 79.1523 | 75.1523 | 26.864 | 26.864 | 26.864 | 65 | 1 | 1 | 0.94192 | 181.8379 | 1 | 12 | Winter day | 2 | 6 | 2.7975 | 2 | 0.82576 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 13 | 47 | 5 | 13 | 1 | 2 | 40 | 37 | 28 | 6 | 78.3333 | 3 | 81.3333 | 45 | 48 | 81.3333 | 3 | 0.24 | 0.22533 | 0 | 3.4653 | 3 | 3 | 2.8112 | 2.8112 | 0 | 0 | 0 | 2.8112 | 0.028112 | 2.7831 | 2.7831 | 100% | 2 | 0.81125 | 0 | 0.093333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 78.73 | 78.73 | 135 | 77.73 | 35% | 0 | 63.8697 | 7.5904 | 0 | 7.2548 | 0 | 0 | 0 | 75.46 | 27.1133 | 71.46 | 0 | 0 | 75.46 | 71.46 | 25.6761 | 25.6761 | 25.6761 | 65 | 1 | 1 | 0.93708 | 180.9039 | 1 | 13 | Winter day | 2 | 6 | 2.7831 | 2 | 0.81125 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 14 | 48 | 5 | 14 | 1 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.093333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 79.78 | 79.78 | 135 | 78.78 | 35% | 0 | 63.6035 | 7.5525 | 0 | 7.3528 | 0 | 0 | 0 | 75.156 | 27.1394 | 71.156 | 0 | 0 | 75.156 | 71.156 | 25.6949 | 25.6949 | 25.6949 | 65 | 1 | 1 | 0.93241 | 180.0022 | 1 | 14 | Winter day | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 15 | 49 | 5 | 15 | 1 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.093333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 84.39 | 84.39 | 135 | 83.39 | 35% | 0 | 67.2788 | 7.5525 | 0 | 7.7831 | 0 | 0 | 0 | 78.8313 | 28.4665 | 74.8313 | 0 | 0 | 78.8313 | 74.8313 | 27.0221 | 27.0221 | 27.0221 | 65 | 1 | 1 | 0.93241 | 180.0022 | 1 | 15 | Winter day | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 16 | 50 | 5 | 16 | 1 | 2 | 40 | 37 | 28 | 6 | 75 | 3 | 78 | 45 | 48 | 78 | 3 | 0.24 | 0.312 | 0 | 3.552 | 3 | 3 | 2.7837 | 2.7837 | 0 | 0 | 0 | 2.7837 | 0.027837 | 2.7559 | 2.7559 | 100% | 2 | 0.7837 | 0 | 0.093333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 90.11 | 90.11 | 135 | 89.11 | 35% | 0 | 70.6191 | 7.516 | 0 | 8.3169 | 0 | 0 | 0 | 82.1351 | 29.8038 | 78.1351 | 0 | 0 | 82.1351 | 78.1351 | 28.3523 | 28.3523 | 28.3523 | 65 | 1 | 1 | 0.9279 | 179.131 | 1 | 16 | Winter day | 2 | 6 | 2.7559 | 2 | 0.7837 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 17 | 51 | 5 | 17 | 1 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 98.8 | 98.8 | 135 | 97.8 | 20% | 0 | 78.7669 | 7.5525 | 0 | 5.216 | 0 | 0 | 0 | 90.3195 | 32.615 | 86.3195 | 0 | 0 | 90.3195 | 86.3195 | 31.1706 | 31.1706 | 31.1706 | 65 | 1 | 1 | 0.93241 | 180.0022 | 1 | 17 | Winter day | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 18 | 52 | 5 | 18 | 1 | 2 | 40 | 37 | 28 | 6 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.24 | 0.182 | 0 | 3.422 | 3 | 3 | 2.8258 | 2.8258 | 0 | 0 | 0 | 2.8258 | 0.028258 | 2.7975 | 2.7975 | 100% | 2 | 0.82576 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 105.93 | 105.93 | 135 | 104.93 | 20% | 0 | 87.4732 | 7.6296 | 0 | 5.5963 | 0 | 0 | 0 | 99.1027 | 35.4254 | 95.1027 | 0 | 0 | 99.1027 | 95.1027 | 33.9955 | 33.9955 | 33.9955 | 65 | 1 | 1 | 0.94192 | 181.8379 | 1 | 18 | Winter day | 2 | 6 | 2.7975 | 2 | 0.82576 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 19 | 53 | 5 | 19 | 1 | 2 | 40 | 37 | 28 | 6 | 82 | 3 | 85 | 45 | 48 | 85 | 3 | 0.24 | 0.13 | 0 | 3.37 | 3 | 3 | 2.8439 | 2.8439 | 0 | 0 | 0 | 2.8439 | 0.028439 | 2.8154 | 2.8154 | 100% | 2 | 0.84388 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 110.87 | 110.87 | 135 | 109.87 | 20% | 0 | 93.5612 | 7.6785 | 0 | 5.8597 | 0 | 0 | 0 | 105.2397 | 37.3794 | 101.2397 | 0 | 0 | 105.2397 | 101.2397 | 35.9587 | 35.9587 | 35.9587 | 65 | 1 | 1 | 0.94796 | 183.0038 | 1 | 19 | Winter day | 2 | 6 | 2.8154 | 2 | 0.84388 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 20 | 54 | 5 | 20 | 1 | 2 | 40 | 37 | 28 | 6 | 83 | 3 | 86 | 45 | 48 | 86 | 3 | 0.24 | 0.104 | 0 | 3.344 | 3 | 3 | 2.8532 | 2.8532 | 0 | 0 | 0 | 2.8532 | 0.028532 | 2.8247 | 2.8247 | 100% | 2 | 0.85324 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 102.57 | 102.57 | 135 | 101.57 | 20% | 0 | 87.5171 | 7.7038 | 0 | 5.4171 | 0 | 0 | 0 | 99.2208 | 35.126 | 95.2208 | 0 | 0 | 99.2208 | 95.2208 | 33.7099 | 33.7099 | 33.7099 | 65 | 1 | 1 | 0.95108 | 183.6061 | 1 | 20 | Winter day | 2 | 6 | 2.8247 | 2 | 0.85324 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 21 | 55 | 5 | 21 | 1 | 2 | 40 | 37 | 28 | 6 | 84 | 3 | 87 | 45 | 48 | 87 | 3 | 0.24 | 0.078 | 0 | 3.318 | 3 | 3 | 2.8628 | 2.8628 | 0 | 0 | 0 | 2.8628 | 0.028628 | 2.8342 | 2.8342 | 100% | 2 | 0.86281 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 92.97 | 92.97 | 135 | 91.97 | 20% | 0 | 80.2157 | 7.7296 | 0 | 4.9051 | 0 | 0 | 0 | 91.9453 | 32.4415 | 87.9453 | 0 | 0 | 91.9453 | 87.9453 | 31.0302 | 31.0302 | 31.0302 | 65 | 1 | 1 | 0.95427 | 184.222 | 1 | 21 | Winter day | 2 | 6 | 2.8342 | 2 | 0.86281 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 22 | 56 | 5 | 22 | 1 | 2 | 40 | 37 | 28 | 6 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.24 | 0.182 | 0 | 3.422 | 3 | 3 | 2.8258 | 2.8258 | 0 | 0 | 0 | 2.8258 | 0.028258 | 2.7975 | 2.7975 | 100% | 2 | 0.82576 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 86.74 | 86.74 | 135 | 85.74 | 20% | 0 | 71.6268 | 7.6296 | 0 | 4.5728 | 0 | 0 | 0 | 83.2563 | 29.7609 | 79.2563 | 0 | 0 | 83.2563 | 79.2563 | 28.3311 | 28.3311 | 28.3311 | 65 | 1 | 1 | 0.94192 | 181.8379 | 1 | 22 | Winter day | 2 | 6 | 2.7975 | 2 | 0.82576 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 23 | 57 | 5 | 23 | 1 | 2 | 40 | 37 | 28 | 6 | 79 | 3 | 82 | 45 | 48 | 82 | 3 | 0.24 | 0.208 | 0 | 3.448 | 3 | 3 | 2.817 | 2.817 | 0 | 0 | 0 | 2.817 | 0.02817 | 2.7888 | 2.7888 | 100% | 2 | 0.81699 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 85.68 | 85.68 | 135 | 84.68 | 20% | 0 | 70 | 7.6059 | 0 | 4.5163 | 0 | 0 | 0 | 81.6059 | 29.2618 | 77.6059 | 0 | 0 | 81.6059 | 77.6059 | 27.8275 | 27.8275 | 27.8275 | 65 | 1 | 1 | 0.939 | 181.2735 | 1 | 23 | Winter day | 2 | 6 | 2.7888 | 2 | 0.81699 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
1 | Winter day | 24 | 58 | 5 | 24 | 1 | 2 | 40 | 37 | 28 | 6 | 78 | 3 | 81 | 45 | 48 | 81 | 3 | 0.24 | 0.234 | 0 | 3.474 | 3 | 3 | 2.8084 | 2.8084 | 0 | 0 | 0 | 2.8084 | 0.028084 | 2.7803 | 2.7803 | 100% | 2 | 0.80841 | 0 | 0.053333 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 80.13 | 80.13 | 135 | 79.13 | 20% | 0 | 64.7777 | 7.5827 | 0 | 4.2203 | 0 | 0 | 0 | 76.3604 | 27.4646 | 72.3604 | 0 | 0 | 76.3604 | 72.3604 | 26.0259 | 26.0259 | 26.0259 | 65 | 1 | 1 | 0.93614 | 180.721 | 1 | 24 | Winter day | 2 | 6 | 2.7803 | 2 | 0.80841 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 1 | 35 | 6 | 1 | 2 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 82 | 82 | 71 | 81 | 70% | 0 | 72.9321 | 4.103 | 0 | 15.12 | 0 | 0 | 0 | 81.0351 | 28.3288 | 77.0351 | 0 | 0 | 81.0351 | 77.0351 | 26.9304 | 26.9304 | 26.9304 | 60 | 1 | 1 | 0.96314 | 171.6313 | 2 | 1 | Spring / fall weekday | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 2 | 36 | 6 | 2 | 2 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 81.7 | 81.7 | 71 | 80.7 | 70% | 0 | 72.6653 | 4.103 | 0 | 15.064 | 0 | 0 | 0 | 80.7683 | 28.2355 | 76.7683 | 0 | 0 | 80.7683 | 76.7683 | 26.8372 | 26.8372 | 26.8372 | 60 | 1 | 1 | 0.96314 | 171.6313 | 2 | 2 | Spring / fall weekday | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 3 | 37 | 6 | 3 | 2 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 81.46 | 81.46 | 71 | 80.46 | 70% | 0 | 72.4518 | 4.103 | 0 | 15.0192 | 0 | 0 | 0 | 80.5548 | 28.1609 | 76.5548 | 0 | 0 | 80.5548 | 76.5548 | 26.7625 | 26.7625 | 26.7625 | 60 | 1 | 1 | 0.96314 | 171.6313 | 2 | 3 | Spring / fall weekday | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 4 | 38 | 6 | 4 | 2 | 2 | 40 | 37 | 28 | 6 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.24 | -0.034667 | 0 | 3.2053 | 3 | 3 | 2.9069 | 2.9069 | 0 | 0 | 0 | 2.9069 | 0.029069 | 2.8778 | 2.8778 | 100% | 2 | 0.90689 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 80.74 | 80.74 | 71 | 79.74 | 70% | 0 | 73.2225 | 4.1278 | 0 | 14.8848 | 0 | 0 | 0 | 81.3503 | 28.268 | 77.3503 | 0 | 0 | 81.3503 | 77.3503 | 26.878 | 26.878 | 26.878 | 60 | 1 | 1 | 0.96896 | 172.6694 | 2 | 4 | Spring / fall weekday | 2 | 6 | 2.8778 | 2 | 0.90689 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 5 | 39 | 6 | 5 | 2 | 2 | 40 | 37 | 28 | 6 | 90 | 3 | 93 | 45 | 48 | 93 | 3 | 0.24 | -0.078 | 0 | 3.162 | 3 | 3 | 2.9251 | 2.9251 | 0 | 0 | 0 | 2.9251 | 0.029251 | 2.8958 | 2.8958 | 100% | 2 | 0.92507 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 81.46 | 81.46 | 71 | 80.46 | 70% | 0 | 75.3562 | 4.1536 | 0 | 15.0192 | 0 | 0 | 0 | 83.5098 | 28.838 | 79.5098 | 0 | 0 | 83.5098 | 79.5098 | 27.4567 | 27.4567 | 27.4567 | 60 | 1 | 1 | 0.97502 | 173.7491 | 2 | 5 | Spring / fall weekday | 2 | 6 | 2.8958 | 2 | 0.92507 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 6 | 40 | 6 | 6 | 2 | 2 | 40 | 37 | 28 | 6 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.24 | -0.034667 | 0 | 3.2053 | 3 | 3 | 2.9069 | 2.9069 | 0 | 0 | 0 | 2.9069 | 0.029069 | 2.8778 | 2.8778 | 100% | 2 | 0.90689 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 84.91 | 84.91 | 71 | 83.91 | 70% | 0 | 77.0042 | 4.1278 | 0 | 15.6632 | 0 | 0 | 0 | 85.132 | 29.5821 | 81.132 | 0 | 0 | 85.132 | 81.132 | 28.1921 | 28.1921 | 28.1921 | 60 | 1 | 1 | 0.96896 | 172.6694 | 2 | 6 | Spring / fall weekday | 2 | 6 | 2.8778 | 2 | 0.90689 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 7 | 41 | 6 | 7 | 2 | 2 | 40 | 37 | 28 | 6 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.24 | -0.034667 | 0 | 3.2053 | 3 | 3 | 2.9069 | 2.9069 | 0 | 0 | 0 | 2.9069 | 0.029069 | 2.8778 | 2.8778 | 100% | 2 | 0.90689 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 94.98 | 94.98 | 71 | 93.98 | 70% | 0 | 86.1366 | 4.1278 | 0 | 17.5429 | 0 | 0 | 0 | 94.2644 | 32.7555 | 90.2644 | 0 | 0 | 94.2644 | 90.2644 | 31.3655 | 31.3655 | 31.3655 | 60 | 1 | 1 | 0.96896 | 172.6694 | 2 | 7 | Spring / fall weekday | 2 | 6 | 2.8778 | 2 | 0.90689 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 8 | 42 | 6 | 8 | 2 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 117.64 | 117.64 | 71 | 116.64 | 70% | 0 | 104.6309 | 4.103 | 0 | 21.7728 | 0 | 0 | 0 | 112.7339 | 39.4102 | 108.7339 | 0 | 0 | 112.7339 | 108.7339 | 38.0119 | 38.0119 | 38.0119 | 60 | 1 | 1 | 0.96314 | 171.6313 | 2 | 8 | Spring / fall weekday | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 9 | 43 | 6 | 9 | 2 | 2 | 40 | 37 | 28 | 6 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.24 | 0.052 | 0 | 3.292 | 3 | 3 | 2.8726 | 2.8726 | 0 | 0 | 0 | 2.8726 | 0.028726 | 2.8439 | 2.8439 | 100% | 2 | 0.8726 | 0 | 0.18667 | -4.1448e-17 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 119.7 | 119.7 | 71 | 118.7 | 70% | 0 | 104.4503 | 4.0791 | 0 | 22.1573 | -4.9199e-15 | 0 | 0 | 112.5294 | 39.569 | 108.5294 | 0 | 0 | 112.5294 | 108.5294 | 38.1625 | 38.1625 | 38.1625 | 60 | 1 | 1 | 0.95753 | 170.6325 | 2 | 9 | Spring / fall weekday | 2 | 6 | 2.8439 | 2 | 0.8726 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 10 | 44 | 6 | 10 | 2 | 2 | 40 | 37 | 28 | 6 | 83.3333 | 3 | 86.3333 | 45 | 48 | 86.3333 | 3 | 0.24 | 0.095333 | 0 | 3.3353 | 3 | 3 | 2.8564 | 2.8564 | 0 | 0 | 0 | 2.8564 | 0.028564 | 2.8278 | 2.8278 | 100% | 2 | 0.85641 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 98.21 | 98.21 | 71 | 97.21 | 85% | 0 | 84.1079 | 4.0561 | 0 | 22.0343 | 0 | 0 | 0 | 92.164 | 32.5916 | 88.164 | 0 | 0 | 92.164 | 88.164 | 31.1771 | 31.1771 | 31.1771 | 60 | 1 | 1 | 0.95214 | 169.6707 | 2 | 10 | Spring / fall weekday | 2 | 6 | 2.8278 | 2 | 0.85641 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 11 | 45 | 6 | 11 | 2 | 2 | 40 | 37 | 28 | 6 | 81.6667 | 3 | 84.6667 | 45 | 48 | 84.6667 | 3 | 0.24 | 0.13867 | 0 | 3.3787 | 3 | 3 | 2.8408 | 2.8408 | 0 | 0 | 0 | 2.8408 | 0.028408 | 2.8124 | 2.8124 | 100% | 2 | 0.84081 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 86.92 | 86.92 | 71 | 85.92 | 85% | 0 | 73.083 | 4.0339 | 0 | 19.4752 | 0 | 0 | 0 | 81.1169 | 28.8426 | 77.1169 | 0 | 0 | 81.1169 | 77.1169 | 27.4203 | 27.4203 | 27.4203 | 60 | 1 | 1 | 0.94694 | 168.7439 | 2 | 11 | Spring / fall weekday | 2 | 6 | 2.8124 | 2 | 0.84081 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 12 | 46 | 6 | 12 | 2 | 2 | 40 | 37 | 28 | 6 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.24 | 0.182 | 0 | 3.422 | 3 | 3 | 2.8258 | 2.8258 | 0 | 0 | 0 | 2.8258 | 0.028258 | 2.7975 | 2.7975 | 100% | 2 | 0.82576 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 83.02 | 83.02 | 71 | 82.02 | 85% | 0 | 68.5549 | 4.0126 | 0 | 18.5912 | 0 | 0 | 0 | 76.5675 | 27.3699 | 72.5675 | 0 | 0 | 76.5675 | 72.5675 | 25.9401 | 25.9401 | 25.9401 | 60 | 1 | 1 | 0.94192 | 167.8504 | 2 | 12 | Spring / fall weekday | 2 | 6 | 2.7975 | 2 | 0.82576 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 13 | 47 | 6 | 13 | 2 | 2 | 40 | 37 | 28 | 6 | 78.3333 | 3 | 81.3333 | 45 | 48 | 81.3333 | 3 | 0.24 | 0.22533 | 0 | 3.4653 | 3 | 3 | 2.8112 | 2.8112 | 0 | 0 | 0 | 2.8112 | 0.028112 | 2.7831 | 2.7831 | 100% | 2 | 0.81125 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 80.35 | 80.35 | 71 | 79.35 | 85% | 0 | 65.1839 | 3.992 | 0 | 17.986 | 0 | 0 | 0 | 73.1759 | 26.2926 | 69.1759 | 0 | 0 | 73.1759 | 69.1759 | 24.8554 | 24.8554 | 24.8554 | 60 | 1 | 1 | 0.93708 | 166.9882 | 2 | 13 | Spring / fall weekday | 2 | 6 | 2.7831 | 2 | 0.81125 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 14 | 48 | 6 | 14 | 2 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 80.29 | 80.29 | 71 | 79.29 | 85% | 0 | 64.0101 | 3.9721 | 0 | 17.9724 | 0 | 0 | 0 | 71.9822 | 25.9933 | 67.9822 | 0 | 0 | 71.9822 | 67.9822 | 24.5488 | 24.5488 | 24.5488 | 60 | 1 | 1 | 0.93241 | 166.1558 | 2 | 14 | Spring / fall weekday | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 15 | 49 | 6 | 15 | 2 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 81.64 | 81.64 | 71 | 80.64 | 85% | 0 | 65.0864 | 3.9721 | 0 | 18.2784 | 0 | 0 | 0 | 73.0584 | 26.3819 | 69.0584 | 0 | 0 | 73.0584 | 69.0584 | 24.9375 | 24.9375 | 24.9375 | 60 | 1 | 1 | 0.93241 | 166.1558 | 2 | 15 | Spring / fall weekday | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 16 | 50 | 6 | 16 | 2 | 2 | 40 | 37 | 28 | 6 | 75 | 3 | 78 | 45 | 48 | 78 | 3 | 0.24 | 0.312 | 0 | 3.552 | 3 | 3 | 2.7837 | 2.7837 | 0 | 0 | 0 | 2.7837 | 0.027837 | 2.7559 | 2.7559 | 100% | 2 | 0.7837 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 83.26 | 83.26 | 71 | 82.26 | 85% | 0 | 65.2508 | 3.9529 | 0 | 18.6456 | 0 | 0 | 0 | 73.2036 | 26.5629 | 69.2036 | 0 | 0 | 73.2036 | 69.2036 | 25.1114 | 25.1114 | 25.1114 | 60 | 1 | 1 | 0.9279 | 165.3517 | 2 | 16 | Spring / fall weekday | 2 | 6 | 2.7559 | 2 | 0.7837 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 17 | 51 | 6 | 17 | 2 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 92.06 | 92.06 | 71 | 91.06 | 85% | 0 | 73.3936 | 3.9721 | 0 | 20.6403 | 0 | 0 | 0 | 81.3656 | 29.3817 | 77.3656 | 0 | 0 | 81.3656 | 77.3656 | 27.9373 | 27.9373 | 27.9373 | 60 | 1 | 1 | 0.93241 | 166.1558 | 2 | 17 | Spring / fall weekday | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 18 | 52 | 6 | 18 | 2 | 2 | 40 | 37 | 28 | 6 | 78.3333 | 3 | 81.3333 | 45 | 48 | 81.3333 | 3 | 0.24 | 0.22533 | 0 | 3.4653 | 3 | 3 | 2.8112 | 2.8112 | 0 | 0 | 0 | 2.8112 | 0.028112 | 2.7831 | 2.7831 | 100% | 2 | 0.81125 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 111 | 111 | 71 | 110 | 75% | 0 | 90.0487 | 3.992 | 0 | 22 | 0 | 0 | 0 | 98.0406 | 35.2267 | 94.0406 | 0 | 0 | 98.0406 | 94.0406 | 33.7894 | 33.7894 | 33.7894 | 60 | 1 | 1 | 0.93708 | 166.9882 | 2 | 18 | Spring / fall weekday | 2 | 6 | 2.7831 | 2 | 0.81125 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 19 | 53 | 6 | 19 | 2 | 2 | 40 | 37 | 28 | 6 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.24 | 0.182 | 0 | 3.422 | 3 | 3 | 2.8258 | 2.8258 | 0 | 0 | 0 | 2.8258 | 0.028258 | 2.7975 | 2.7975 | 100% | 2 | 0.82576 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 130.58 | 130.58 | 71 | 129.58 | 75% | 0 | 107.8282 | 4.0126 | 0 | 25.916 | 0 | 0 | 0 | 115.8408 | 41.4086 | 111.8408 | 0 | 0 | 115.8408 | 111.8408 | 39.9788 | 39.9788 | 39.9788 | 60 | 1 | 1 | 0.94192 | 167.8504 | 2 | 19 | Spring / fall weekday | 2 | 6 | 2.7975 | 2 | 0.82576 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 20 | 54 | 6 | 20 | 2 | 2 | 40 | 37 | 28 | 6 | 81.6667 | 3 | 84.6667 | 45 | 48 | 84.6667 | 3 | 0.24 | 0.13867 | 0 | 3.3787 | 3 | 3 | 2.8408 | 2.8408 | 0 | 0 | 0 | 2.8408 | 0.028408 | 2.8124 | 2.8124 | 100% | 2 | 0.84081 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 130.25 | 130.25 | 71 | 129.25 | 75% | 0 | 109.5151 | 4.0339 | 0 | 25.85 | 0 | 0 | 0 | 117.5491 | 41.7967 | 113.5491 | 0 | 0 | 117.5491 | 113.5491 | 40.3745 | 40.3745 | 40.3745 | 60 | 1 | 1 | 0.94694 | 168.7439 | 2 | 20 | Spring / fall weekday | 2 | 6 | 2.8124 | 2 | 0.84081 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 21 | 55 | 6 | 21 | 2 | 2 | 40 | 37 | 28 | 6 | 83.3333 | 3 | 86.3333 | 45 | 48 | 86.3333 | 3 | 0.24 | 0.095333 | 0 | 3.3353 | 3 | 3 | 2.8564 | 2.8564 | 0 | 0 | 0 | 2.8564 | 0.028564 | 2.8278 | 2.8278 | 100% | 2 | 0.85641 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 104.4 | 104.4 | 71 | 103.4 | 75% | 0 | 89.4091 | 4.0561 | 0 | 20.68 | 0 | 0 | 0 | 97.4652 | 34.4662 | 93.4652 | 0 | 0 | 97.4652 | 93.4652 | 33.0517 | 33.0517 | 33.0517 | 60 | 1 | 1 | 0.95214 | 169.6707 | 2 | 21 | Spring / fall weekday | 2 | 6 | 2.8278 | 2 | 0.85641 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 22 | 56 | 6 | 22 | 2 | 2 | 40 | 37 | 28 | 6 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.24 | 0.052 | 0 | 3.292 | 3 | 3 | 2.8726 | 2.8726 | 0 | 0 | 0 | 2.8726 | 0.028726 | 2.8439 | 2.8439 | 100% | 2 | 0.8726 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 91.15 | 91.15 | 71 | 90.15 | 75% | 0 | 79.5375 | 4.0791 | 0 | 18.03 | 0 | 0 | 0 | 87.6166 | 30.8089 | 83.6166 | 0 | 0 | 87.6166 | 83.6166 | 29.4024 | 29.4024 | 29.4024 | 60 | 1 | 1 | 0.95753 | 170.6325 | 2 | 22 | Spring / fall weekday | 2 | 6 | 2.8439 | 2 | 0.8726 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 23 | 57 | 6 | 23 | 2 | 2 | 40 | 37 | 28 | 6 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.24 | 0.052 | 0 | 3.292 | 3 | 3 | 2.8726 | 2.8726 | 0 | 0 | 0 | 2.8726 | 0.028726 | 2.8439 | 2.8439 | 100% | 2 | 0.8726 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 88.98 | 88.98 | 71 | 87.98 | 75% | 0 | 77.644 | 4.0791 | 0 | 17.596 | 0 | 0 | 0 | 85.7231 | 30.1431 | 81.7231 | 0 | 0 | 85.7231 | 81.7231 | 28.7365 | 28.7365 | 28.7365 | 60 | 1 | 1 | 0.95753 | 170.6325 | 2 | 23 | Spring / fall weekday | 2 | 6 | 2.8439 | 2 | 0.8726 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
2 | Spring / fall weekday | 24 | 58 | 6 | 24 | 2 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 85.34 | 85.34 | 71 | 84.34 | 75% | 0 | 75.9028 | 4.103 | 0 | 16.868 | 0 | 0 | 0 | 84.0057 | 29.3673 | 80.0057 | 0 | 0 | 84.0057 | 80.0057 | 27.9689 | 27.9689 | 27.9689 | 60 | 1 | 1 | 0.96314 | 171.6313 | 2 | 24 | Spring / fall weekday | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 1 | 35 | 7 | 1 | 3 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 92.85 | 92.85 | 71 | 91.85 | 70% | 0 | 82.5823 | 4.103 | 0 | 17.1453 | 0 | 0 | 0 | 90.6852 | 31.7023 | 86.6852 | 0 | 0 | 90.6852 | 86.6852 | 30.304 | 30.304 | 30.304 | 60 | 1 | 1 | 0.96314 | 171.6313 | 3 | 1 | Spring / fall weekend | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 2 | 36 | 7 | 2 | 3 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 81.59 | 81.59 | 71 | 80.59 | 70% | 0 | 72.5674 | 4.103 | 0 | 15.0435 | 0 | 0 | 0 | 80.6704 | 28.2013 | 76.6704 | 0 | 0 | 80.6704 | 76.6704 | 26.8029 | 26.8029 | 26.8029 | 60 | 1 | 1 | 0.96314 | 171.6313 | 3 | 2 | Spring / fall weekend | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 3 | 37 | 7 | 3 | 3 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 80.53 | 80.53 | 71 | 79.53 | 70% | 0 | 71.6247 | 4.103 | 0 | 14.8456 | 0 | 0 | 0 | 79.7276 | 27.8717 | 75.7276 | 0 | 0 | 79.7276 | 75.7276 | 26.4734 | 26.4734 | 26.4734 | 60 | 1 | 1 | 0.96314 | 171.6313 | 3 | 3 | Spring / fall weekend | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 4 | 38 | 7 | 4 | 3 | 2 | 40 | 37 | 28 | 6 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.24 | -0.034667 | 0 | 3.2053 | 3 | 3 | 2.9069 | 2.9069 | 0 | 0 | 0 | 2.9069 | 0.029069 | 2.8778 | 2.8778 | 100% | 2 | 0.90689 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 75.4 | 75.4 | 71 | 74.4 | 70% | 0 | 68.3797 | 4.1278 | 0 | 13.888 | 0 | 0 | 0 | 76.5075 | 26.5852 | 72.5075 | 0 | 0 | 76.5075 | 72.5075 | 25.1952 | 25.1952 | 25.1952 | 60 | 1 | 1 | 0.96896 | 172.6694 | 3 | 4 | Spring / fall weekend | 2 | 6 | 2.8778 | 2 | 0.90689 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 5 | 39 | 7 | 5 | 3 | 2 | 40 | 37 | 28 | 6 | 90 | 3 | 93 | 45 | 48 | 93 | 3 | 0.24 | -0.078 | 0 | 3.162 | 3 | 3 | 2.9251 | 2.9251 | 0 | 0 | 0 | 2.9251 | 0.029251 | 2.8958 | 2.8958 | 100% | 2 | 0.92507 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 74.88 | 74.88 | 71 | 73.88 | 70% | 0 | 69.2692 | 4.1536 | 0 | 13.7909 | 0 | 0 | 0 | 77.4228 | 26.7361 | 73.4228 | 0 | 0 | 77.4228 | 73.4228 | 25.3548 | 25.3548 | 25.3548 | 60 | 1 | 1 | 0.97502 | 173.7491 | 3 | 5 | Spring / fall weekend | 2 | 6 | 2.8958 | 2 | 0.92507 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 6 | 40 | 7 | 6 | 3 | 2 | 40 | 37 | 28 | 6 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.24 | -0.034667 | 0 | 3.2053 | 3 | 3 | 2.9069 | 2.9069 | 0 | 0 | 0 | 2.9069 | 0.029069 | 2.8778 | 2.8778 | 100% | 2 | 0.90689 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 74.62 | 74.62 | 71 | 73.62 | 70% | 0 | 67.6723 | 4.1278 | 0 | 13.7424 | 0 | 0 | 0 | 75.8001 | 26.3394 | 71.8001 | 0 | 0 | 75.8001 | 71.8001 | 24.9494 | 24.9494 | 24.9494 | 60 | 1 | 1 | 0.96896 | 172.6694 | 3 | 6 | Spring / fall weekend | 2 | 6 | 2.8778 | 2 | 0.90689 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 7 | 41 | 7 | 7 | 3 | 2 | 40 | 37 | 28 | 6 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.24 | -0.034667 | 0 | 3.2053 | 3 | 3 | 2.9069 | 2.9069 | 0 | 0 | 0 | 2.9069 | 0.029069 | 2.8778 | 2.8778 | 100% | 2 | 0.90689 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 75.43 | 75.43 | 71 | 74.43 | 70% | 0 | 68.4069 | 4.1278 | 0 | 13.8936 | 0 | 0 | 0 | 76.5347 | 26.5946 | 72.5347 | 0 | 0 | 76.5347 | 72.5347 | 25.2047 | 25.2047 | 25.2047 | 60 | 1 | 1 | 0.96896 | 172.6694 | 3 | 7 | Spring / fall weekend | 2 | 6 | 2.8778 | 2 | 0.90689 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 8 | 42 | 7 | 8 | 3 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.18667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 71.53 | 71.53 | 71 | 70.53 | 70% | 0 | 63.6199 | 4.103 | 0 | 13.1656 | 0 | 0 | 0 | 71.7229 | 25.0734 | 67.7229 | 0 | 0 | 71.7229 | 67.7229 | 23.675 | 23.675 | 23.675 | 60 | 1 | 1 | 0.96314 | 171.6313 | 3 | 8 | Spring / fall weekend | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 9 | 43 | 7 | 9 | 3 | 2 | 40 | 37 | 28 | 6 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.24 | 0.052 | 0 | 3.292 | 3 | 3 | 2.8726 | 2.8726 | 0 | 0 | 0 | 2.8726 | 0.028726 | 2.8439 | 2.8439 | 100% | 2 | 0.8726 | 0 | 0.18667 | -4.1448e-17 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 71.88 | 71.88 | 71 | 70.88 | 70% | 0 | 62.7225 | 4.0791 | 0 | 13.2309 | -2.9379e-15 | 0 | 0 | 70.8016 | 24.8962 | 66.8016 | 0 | 0 | 70.8016 | 66.8016 | 23.4896 | 23.4896 | 23.4896 | 60 | 1 | 1 | 0.95753 | 170.6325 | 3 | 9 | Spring / fall weekend | 2 | 6 | 2.8439 | 2 | 0.8726 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 10 | 44 | 7 | 10 | 3 | 2 | 40 | 37 | 28 | 6 | 83.3333 | 3 | 86.3333 | 45 | 48 | 86.3333 | 3 | 0.24 | 0.095333 | 0 | 3.3353 | 3 | 3 | 2.8564 | 2.8564 | 0 | 0 | 0 | 2.8564 | 0.028564 | 2.8278 | 2.8278 | 100% | 2 | 0.85641 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 66.38 | 66.38 | 71 | 65.38 | 85% | 0 | 56.8484 | 4.0561 | 0 | 14.8195 | 0 | 0 | 0 | 64.9045 | 22.9519 | 60.9045 | 0 | 0 | 64.9045 | 60.9045 | 21.5374 | 21.5374 | 21.5374 | 60 | 1 | 1 | 0.95214 | 169.6707 | 3 | 10 | Spring / fall weekend | 2 | 6 | 2.8278 | 2 | 0.85641 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 11 | 45 | 7 | 11 | 3 | 2 | 40 | 37 | 28 | 6 | 81.6667 | 3 | 84.6667 | 45 | 48 | 84.6667 | 3 | 0.24 | 0.13867 | 0 | 3.3787 | 3 | 3 | 2.8408 | 2.8408 | 0 | 0 | 0 | 2.8408 | 0.028408 | 2.8124 | 2.8124 | 100% | 2 | 0.84081 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 43.99 | 43.99 | 71 | 42.99 | 85% | 0 | 36.9871 | 4.0339 | 0 | 9.7444 | 0 | 0 | 0 | 45.0211 | 16.0081 | 41.0211 | 0 | 0 | 45.0211 | 41.0211 | 14.5858 | 14.5858 | 14.5858 | 60 | 1 | 1 | 0.94694 | 168.7439 | 3 | 11 | Spring / fall weekend | 2 | 6 | 2.8124 | 2 | 0.84081 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 12 | 46 | 7 | 12 | 3 | 2 | 40 | 37 | 28 | 6 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.24 | 0.182 | 0 | 3.422 | 3 | 3 | 2.8258 | 2.8258 | 0 | 0 | 0 | 2.8258 | 0.028258 | 2.7975 | 2.7975 | 100% | 2 | 0.82576 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 47.96 | 47.96 | 71 | 46.96 | 85% | 0 | 39.6036 | 4.0126 | 0 | 10.6443 | 0 | 0 | 0 | 47.6162 | 17.021 | 43.6162 | 0 | 0 | 47.6162 | 43.6162 | 15.5911 | 15.5911 | 15.5911 | 60 | 1 | 1 | 0.94192 | 167.8504 | 3 | 12 | Spring / fall weekend | 2 | 6 | 2.7975 | 2 | 0.82576 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 13 | 47 | 7 | 13 | 3 | 2 | 40 | 37 | 28 | 6 | 78.3333 | 3 | 81.3333 | 45 | 48 | 81.3333 | 3 | 0.24 | 0.22533 | 0 | 3.4653 | 3 | 3 | 2.8112 | 2.8112 | 0 | 0 | 0 | 2.8112 | 0.028112 | 2.7831 | 2.7831 | 100% | 2 | 0.81125 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 17.06 | 17.06 | 71 | 16.06 | 85% | 0 | 13.8399 | 3.992 | 0 | 3.6403 | 0 | 0 | 0 | 21.8319 | 7.8443 | 17.8319 | 0 | 0 | 21.8319 | 17.8319 | 6.4071 | 6.4071 | 6.4071 | 60 | 1 | 1 | 0.93708 | 166.9882 | 3 | 13 | Spring / fall weekend | 2 | 6 | 2.7831 | 2 | 0.81125 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 14 | 48 | 7 | 14 | 3 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 11.28 | 11.28 | 71 | 10.28 | 85% | 0 | 8.9928 | 3.9721 | 0 | 2.3301 | 0 | 0 | 0 | 16.9649 | 6.1261 | 12.9649 | 0 | 0 | 16.9649 | 12.9649 | 4.6817 | 4.6817 | 4.6817 | 60 | 1 | 1 | 0.93241 | 166.1558 | 3 | 14 | Spring / fall weekend | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 15 | 49 | 7 | 15 | 3 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 10.1 | 10.1 | 71 | 9.1 | 85% | 0 | 8.0521 | 3.9721 | 0 | 2.0627 | 0 | 0 | 0 | 16.0242 | 5.7864 | 12.0242 | 0 | 0 | 16.0242 | 12.0242 | 4.342 | 4.342 | 4.342 | 60 | 1 | 1 | 0.93241 | 166.1558 | 3 | 15 | Spring / fall weekend | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 16 | 50 | 7 | 16 | 3 | 2 | 40 | 37 | 28 | 6 | 75 | 3 | 78 | 45 | 48 | 78 | 3 | 0.24 | 0.312 | 0 | 3.552 | 3 | 3 | 2.7837 | 2.7837 | 0 | 0 | 0 | 2.7837 | 0.027837 | 2.7559 | 2.7559 | 100% | 2 | 0.7837 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 11.75 | 11.75 | 71 | 10.75 | 85% | 0 | 9.2085 | 3.9529 | 0 | 2.4367 | 0 | 0 | 0 | 17.1613 | 6.2272 | 13.1613 | 0 | 0 | 17.1613 | 13.1613 | 4.7758 | 4.7758 | 4.7758 | 60 | 1 | 1 | 0.9279 | 165.3517 | 3 | 16 | Spring / fall weekend | 2 | 6 | 2.7559 | 2 | 0.7837 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 17 | 51 | 7 | 17 | 3 | 2 | 40 | 37 | 28 | 6 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.24 | 0.26867 | 0 | 3.5087 | 3 | 3 | 2.7972 | 2.7972 | 0 | 0 | 0 | 2.7972 | 0.027972 | 2.7693 | 2.7693 | 100% | 2 | 0.79724 | 0 | 0.22667 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 17.01 | 17.01 | 71 | 16.01 | 85% | 0 | 13.561 | 3.9721 | 0 | 3.6289 | 0 | 0 | 0 | 21.5331 | 7.7757 | 17.5331 | 0 | 0 | 21.5331 | 17.5331 | 6.3313 | 6.3313 | 6.3313 | 60 | 1 | 1 | 0.93241 | 166.1558 | 3 | 17 | Spring / fall weekend | 2 | 6 | 2.7693 | 2 | 0.79724 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 18 | 52 | 7 | 18 | 3 | 2 | 40 | 37 | 28 | 6 | 78.3333 | 3 | 81.3333 | 45 | 48 | 81.3333 | 3 | 0.24 | 0.22533 | 0 | 3.4653 | 3 | 3 | 2.8112 | 2.8112 | 0 | 0 | 0 | 2.8112 | 0.028112 | 2.7831 | 2.7831 | 100% | 2 | 0.81125 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 69.22 | 69.22 | 71 | 68.22 | 75% | 0 | 56.1547 | 3.992 | 0 | 13.644 | 0 | 0 | 0 | 64.1467 | 23.0483 | 60.1467 | 0 | 0 | 64.1467 | 60.1467 | 21.6111 | 21.6111 | 21.6111 | 60 | 1 | 1 | 0.93708 | 166.9882 | 3 | 18 | Spring / fall weekend | 2 | 6 | 2.7831 | 2 | 0.81125 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 19 | 53 | 7 | 19 | 3 | 2 | 40 | 37 | 28 | 6 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.24 | 0.182 | 0 | 3.422 | 3 | 3 | 2.8258 | 2.8258 | 0 | 0 | 0 | 2.8258 | 0.028258 | 2.7975 | 2.7975 | 100% | 2 | 0.82576 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 85.6 | 85.6 | 71 | 84.6 | 75% | 0 | 70.6854 | 4.0126 | 0 | 16.92 | 0 | 0 | 0 | 78.698 | 28.1315 | 74.698 | 0 | 0 | 78.698 | 74.698 | 26.7016 | 26.7016 | 26.7016 | 60 | 1 | 1 | 0.94192 | 167.8504 | 3 | 19 | Spring / fall weekend | 2 | 6 | 2.7975 | 2 | 0.82576 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 20 | 54 | 7 | 20 | 3 | 2 | 40 | 37 | 28 | 6 | 81.6667 | 3 | 84.6667 | 45 | 48 | 84.6667 | 3 | 0.24 | 0.13867 | 0 | 3.3787 | 3 | 3 | 2.8408 | 2.8408 | 0 | 0 | 0 | 2.8408 | 0.028408 | 2.8124 | 2.8124 | 100% | 2 | 0.84081 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 100.36 | 100.36 | 71 | 99.36 | 75% | 0 | 84.3834 | 4.0339 | 0 | 19.872 | 0 | 0 | 0 | 92.4174 | 32.8607 | 88.4174 | 0 | 0 | 92.4174 | 88.4174 | 31.4384 | 31.4384 | 31.4384 | 60 | 1 | 1 | 0.94694 | 168.7439 | 3 | 20 | Spring / fall weekend | 2 | 6 | 2.8124 | 2 | 0.84081 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 21 | 55 | 7 | 21 | 3 | 2 | 40 | 37 | 28 | 6 | 83.3333 | 3 | 86.3333 | 45 | 48 | 86.3333 | 3 | 0.24 | 0.095333 | 0 | 3.3353 | 3 | 3 | 2.8564 | 2.8564 | 0 | 0 | 0 | 2.8564 | 0.028564 | 2.8278 | 2.8278 | 100% | 2 | 0.85641 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 106.26 | 106.26 | 71 | 105.26 | 75% | 0 | 91.002 | 4.0561 | 0 | 21.052 | 0 | 0 | 0 | 99.0581 | 35.0295 | 95.0581 | 0 | 0 | 99.0581 | 95.0581 | 33.615 | 33.615 | 33.615 | 60 | 1 | 1 | 0.95214 | 169.6707 | 3 | 21 | Spring / fall weekend | 2 | 6 | 2.8278 | 2 | 0.85641 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 22 | 56 | 7 | 22 | 3 | 2 | 40 | 37 | 28 | 6 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.24 | 0.052 | 0 | 3.292 | 3 | 3 | 2.8726 | 2.8726 | 0 | 0 | 0 | 2.8726 | 0.028726 | 2.8439 | 2.8439 | 100% | 2 | 0.8726 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 102.07 | 102.07 | 71 | 101.07 | 75% | 0 | 89.0663 | 4.0791 | 0 | 20.214 | 0 | 0 | 0 | 97.1454 | 34.1595 | 93.1454 | 0 | 0 | 97.1454 | 93.1454 | 32.753 | 32.753 | 32.753 | 60 | 1 | 1 | 0.95753 | 170.6325 | 3 | 22 | Spring / fall weekend | 2 | 6 | 2.8439 | 2 | 0.8726 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 23 | 57 | 7 | 23 | 3 | 2 | 40 | 37 | 28 | 6 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.24 | 0.052 | 0 | 3.292 | 3 | 3 | 2.8726 | 2.8726 | 0 | 0 | 0 | 2.8726 | 0.028726 | 2.8439 | 2.8439 | 100% | 2 | 0.8726 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 100.41 | 100.41 | 71 | 99.41 | 75% | 0 | 87.6178 | 4.0791 | 0 | 19.882 | 0 | 0 | 0 | 95.6969 | 33.6502 | 91.6969 | 0 | 0 | 95.6969 | 91.6969 | 32.2437 | 32.2437 | 32.2437 | 60 | 1 | 1 | 0.95753 | 170.6325 | 3 | 23 | Spring / fall weekend | 2 | 6 | 2.8439 | 2 | 0.8726 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
3 | Spring / fall weekend | 24 | 58 | 7 | 24 | 3 | 2 | 40 | 37 | 28 | 6 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.24 | 0.0086667 | 0 | 3.2487 | 3 | 3 | 2.8894 | 2.8894 | 0 | 0 | 0 | 2.8894 | 0.028894 | 2.8605 | 2.8605 | 100% | 2 | 0.88942 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 2 | 1 | 4 | 0 | 99.46 | 99.46 | 71 | 98.46 | 75% | 0 | 88.4613 | 4.103 | 0 | 19.692 | 0 | 0 | 0 | 96.5643 | 33.7576 | 92.5643 | 0 | 0 | 96.5643 | 92.5643 | 32.3592 | 32.3592 | 32.3592 | 60 | 1 | 1 | 0.96314 | 171.6313 | 3 | 24 | Spring / fall weekend | 2 | 6 | 2.8605 | 2 | 0.88942 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 1 | 35 | 8 | 1 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 101.11 | 101.11 | 60 | 100.11 | 100% | 0 | 54.4106 | 2.5456 | 0 | 21.1324 | 5.5636 | 0 | 0 | 60.9562 | 29.0253 | 56.9562 | 0 | 0 | 60.9562 | 56.9562 | 27.1206 | 27.1206 | 27.1206 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 1 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 2 | 36 | 8 | 2 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 91.45 | 91.45 | 60 | 90.45 | 100% | 0 | 49.2123 | 2.5456 | 0 | 19.0932 | 5.0268 | 0 | 0 | 55.7578 | 26.55 | 51.7578 | 0 | 0 | 55.7578 | 51.7578 | 24.6453 | 24.6453 | 24.6453 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 2 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 3 | 37 | 8 | 3 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 90.91 | 90.91 | 60 | 89.91 | 100% | 0 | 48.9217 | 2.5456 | 0 | 18.9792 | 4.9968 | 0 | 0 | 55.4673 | 26.4116 | 51.4673 | 0 | 0 | 55.4673 | 51.4673 | 24.507 | 24.507 | 24.507 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 3 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 4 | 38 | 8 | 4 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 90.29 | 90.29 | 60 | 89.29 | 100% | 0 | 48.588 | 2.5456 | 0 | 18.8484 | 4.9623 | 0 | 0 | 55.1336 | 26.2528 | 51.1336 | 0 | 0 | 55.1336 | 51.1336 | 24.3481 | 24.3481 | 24.3481 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 4 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 5 | 39 | 8 | 5 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 94.38 | 94.38 | 60 | 93.38 | 100% | 0 | 50.789 | 2.5456 | 0 | 19.7117 | 5.1896 | 0 | 0 | 57.3346 | 27.3008 | 53.3346 | 0 | 0 | 57.3346 | 53.3346 | 25.3961 | 25.3961 | 25.3961 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 5 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 6 | 40 | 8 | 6 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 102.38 | 102.38 | 60 | 101.38 | 100% | 0 | 55.0941 | 2.5456 | 0 | 21.4005 | 5.6342 | 0 | 0 | 61.6396 | 29.3507 | 57.6396 | 0 | 0 | 61.6396 | 57.6396 | 27.446 | 27.446 | 27.446 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 6 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 7 | 41 | 8 | 7 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 126.6 | 126.6 | 60 | 125.6 | 100% | 0 | 68.1276 | 2.5456 | 0 | 26.5131 | 6.9802 | 0 | 0 | 74.6732 | 35.5569 | 70.6732 | 0 | 0 | 74.6732 | 70.6732 | 33.6522 | 33.6522 | 33.6522 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 7 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 8 | 42 | 8 | 8 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 121.72 | 121.72 | 60 | 120.72 | 100% | 0 | 65.5016 | 2.5456 | 0 | 25.483 | 6.709 | 0 | 0 | 72.0471 | 34.3064 | 68.0471 | 0 | 0 | 72.0471 | 68.0471 | 32.4017 | 32.4017 | 32.4017 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 8 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 9 | 43 | 8 | 9 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 109.4 | 109.4 | 60 | 108.4 | 100% | 0 | 58.8718 | 2.5456 | 0 | 22.8823 | 6.0243 | 0 | 0 | 65.4173 | 31.1495 | 61.4173 | 0 | 0 | 65.4173 | 61.4173 | 29.2449 | 29.2449 | 29.2449 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 9 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 10 | 44 | 8 | 10 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 92.43 | 92.43 | 60 | 91.43 | 100% | 0 | 49.7396 | 2.5456 | 0 | 19.3001 | 5.0812 | 0 | 0 | 56.2852 | 26.8011 | 52.2852 | 0 | 0 | 56.2852 | 52.2852 | 24.8965 | 24.8965 | 24.8965 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 10 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 11 | 45 | 8 | 11 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 81 | 81 | 60 | 80 | 100% | 0 | 43.5888 | 2.5456 | 0 | 16.8873 | 4.446 | 0 | 0 | 50.1344 | 23.8723 | 46.1344 | 0 | 0 | 50.1344 | 46.1344 | 21.9676 | 21.9676 | 21.9676 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 11 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 12 | 46 | 8 | 12 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 69.75 | 69.75 | 60 | 68.75 | 100% | 0 | 37.5348 | 2.5456 | 0 | 14.5126 | 3.8208 | 0 | 0 | 44.0804 | 20.9896 | 40.0804 | 0 | 0 | 44.0804 | 40.0804 | 19.0849 | 19.0849 | 19.0849 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 12 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 13 | 47 | 8 | 13 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 55.34 | 55.34 | 60 | 54.34 | 100% | 0 | 29.7803 | 2.5456 | 0 | 11.4707 | 3.0199 | 0 | 0 | 36.3259 | 17.2971 | 32.3259 | 0 | 0 | 36.3259 | 32.3259 | 15.3925 | 15.3925 | 15.3925 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 13 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 14 | 48 | 8 | 14 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 47.5 | 47.5 | 60 | 46.5 | 100% | 0 | 25.5613 | 2.5456 | 0 | 9.8158 | 2.5842 | 0 | 0 | 32.1069 | 15.2882 | 28.1069 | 0 | 0 | 32.1069 | 28.1069 | 13.3836 | 13.3836 | 13.3836 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 14 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 15 | 49 | 8 | 15 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 47.2 | 47.2 | 60 | 46.2 | 100% | 0 | 25.3999 | 2.5456 | 0 | 9.7524 | 2.5676 | 0 | 0 | 31.9455 | 15.2113 | 27.9455 | 0 | 0 | 31.9455 | 27.9455 | 13.3067 | 13.3067 | 13.3067 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 15 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 16 | 50 | 8 | 16 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 53.54 | 53.54 | 60 | 52.54 | 100% | 0 | 28.8116 | 2.5456 | 0 | 11.0908 | 2.9199 | 0 | 0 | 35.3572 | 16.8359 | 31.3572 | 0 | 0 | 35.3572 | 31.3572 | 14.9313 | 14.9313 | 14.9313 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 16 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 17 | 51 | 8 | 17 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 74.79 | 74.79 | 60 | 73.79 | 100% | 0 | 40.247 | 2.5456 | 0 | 15.5765 | 4.1009 | 0 | 0 | 46.7926 | 22.281 | 42.7926 | 0 | 0 | 46.7926 | 42.7926 | 20.3764 | 20.3764 | 20.3764 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 17 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 18 | 52 | 8 | 18 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 88.34 | 88.34 | 60 | 87.34 | 100% | 0 | 47.5387 | 2.5456 | 0 | 18.4367 | 4.8539 | 0 | 0 | 54.0843 | 25.7531 | 50.0843 | 0 | 0 | 54.0843 | 50.0843 | 23.8484 | 23.8484 | 23.8484 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 18 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 19 | 53 | 8 | 19 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 102.61 | 102.61 | 60 | 101.61 | 100% | 0 | 55.2178 | 2.5456 | 0 | 21.449 | 5.647 | 0 | 0 | 61.7634 | 29.4096 | 57.7634 | 0 | 0 | 61.7634 | 57.7634 | 27.505 | 27.505 | 27.505 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 19 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 20 | 54 | 8 | 20 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 132.02 | 132.02 | 60 | 131.02 | 100% | 0 | 71.0443 | 2.5456 | 0 | 27.6572 | 7.2814 | 0 | 0 | 77.5899 | 36.9457 | 73.5899 | 0 | 0 | 77.5899 | 73.5899 | 35.041 | 35.041 | 35.041 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 20 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 21 | 55 | 8 | 21 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0 | 0.26667 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 201.46 | 201.46 | 60 | 200.46 | 100% | 0 | 108.4123 | 2.5456 | 0 | 0 | 53.456 | 0 | 0 | 114.9579 | 54.739 | 110.9579 | 0 | 0 | 114.9579 | 110.9579 | 52.8344 | 52.8344 | 52.8344 | 40 | 0 | 0 | 0 | 84.0043 | 4 | 21 | Summer weekday | 2 | 6 | 0 | 0 | 0 | 0 | 0.03 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 22 | 56 | 8 | 22 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 131 | 131 | 60 | 130 | 100% | 0 | 70.4954 | 2.5456 | 0 | 27.4419 | 7.2248 | 0 | 0 | 77.041 | 36.6843 | 73.041 | 0 | 0 | 77.041 | 73.041 | 34.7797 | 34.7797 | 34.7797 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 22 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 23 | 57 | 8 | 23 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 117.86 | 117.86 | 60 | 116.86 | 100% | 0 | 63.4244 | 2.5456 | 0 | 24.6682 | 6.4945 | 0 | 0 | 69.9699 | 33.3173 | 65.9699 | 0 | 0 | 69.9699 | 65.9699 | 31.4127 | 31.4127 | 31.4127 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 23 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
4 | Summer weekday | 24 | 58 | 8 | 24 | 4 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 102.55 | 102.55 | 60 | 101.55 | 100% | 0 | 55.1855 | 2.5456 | 0 | 21.4364 | 5.6436 | 0 | 0 | 61.7311 | 29.3943 | 57.7311 | 0 | 0 | 61.7311 | 57.7311 | 27.4896 | 27.4896 | 27.4896 | 40 | 1 | 1 | 0.70711 | 84.0043 | 4 | 24 | Summer weekday | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 1 | 35 | 9 | 1 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 101.49 | 101.49 | 60 | 100.49 | 100% | 0 | 54.6151 | 2.5456 | 0 | 21.2126 | 5.5847 | 0 | 0 | 61.1607 | 29.1227 | 57.1607 | 0 | 0 | 61.1607 | 57.1607 | 27.218 | 27.218 | 27.218 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 1 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 2 | 36 | 9 | 2 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 90.25 | 90.25 | 60 | 89.25 | 100% | 0 | 48.5665 | 2.5456 | 0 | 18.8399 | 4.9601 | 0 | 0 | 55.1121 | 26.2425 | 51.1121 | 0 | 0 | 55.1121 | 51.1121 | 24.3378 | 24.3378 | 24.3378 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 2 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 3 | 37 | 9 | 3 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 82.24 | 82.24 | 60 | 81.24 | 100% | 0 | 44.2561 | 2.5456 | 0 | 17.1491 | 4.5149 | 0 | 0 | 50.8016 | 24.19 | 46.8016 | 0 | 0 | 50.8016 | 46.8016 | 22.2854 | 22.2854 | 22.2854 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 3 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 4 | 38 | 9 | 4 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 81.67 | 81.67 | 60 | 80.67 | 100% | 0 | 43.9493 | 2.5456 | 0 | 17.0288 | 4.4832 | 0 | 0 | 50.4949 | 24.044 | 46.4949 | 0 | 0 | 50.4949 | 46.4949 | 22.1393 | 22.1393 | 22.1393 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 4 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 5 | 39 | 9 | 5 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 77.94 | 77.94 | 60 | 76.94 | 100% | 0 | 41.9421 | 2.5456 | 0 | 16.2414 | 4.2759 | 0 | 0 | 48.4877 | 23.0882 | 44.4877 | 0 | 0 | 48.4877 | 44.4877 | 21.1835 | 21.1835 | 21.1835 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 5 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 6 | 40 | 9 | 6 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 73.09 | 73.09 | 60 | 72.09 | 100% | 0 | 39.3321 | 2.5456 | 0 | 15.2176 | 4.0064 | 0 | 0 | 45.8777 | 21.8454 | 41.8777 | 0 | 0 | 45.8777 | 41.8777 | 19.9408 | 19.9408 | 19.9408 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 6 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 7 | 41 | 9 | 7 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 68.9 | 68.9 | 60 | 67.9 | 100% | 0 | 37.0774 | 2.5456 | 0 | 14.3331 | 3.7735 | 0 | 0 | 43.6229 | 20.7718 | 39.6229 | 0 | 0 | 43.6229 | 39.6229 | 18.8671 | 18.8671 | 18.8671 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 7 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 8 | 42 | 9 | 8 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 57.35 | 57.35 | 60 | 56.35 | 100% | 0 | 30.8619 | 2.5456 | 0 | 11.895 | 3.1317 | 0 | 0 | 37.4075 | 17.8122 | 33.4075 | 0 | 0 | 37.4075 | 33.4075 | 15.9075 | 15.9075 | 15.9075 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 8 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 9 | 43 | 9 | 9 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 30.77 | 30.77 | 60 | 29.77 | 100% | 0 | 16.5584 | 2.5456 | 0 | 6.2842 | 1.6545 | 0 | 0 | 23.1039 | 11.0013 | 19.1039 | 0 | 0 | 23.1039 | 19.1039 | 9.0966 | 9.0966 | 9.0966 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 9 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 10 | 44 | 9 | 10 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 15.24 | 15.24 | 60 | 14.24 | 100% | 0 | 8.2011 | 2.5456 | 0 | 3.0059 | 0.79139 | 0 | 0 | 14.7467 | 7.0219 | 10.7467 | 0 | 0 | 14.7467 | 10.7467 | 5.1172 | 5.1172 | 5.1172 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 10 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 11 | 45 | 9 | 11 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 11 | 11 | 60 | 10 | 100% | 0 | 5.9195 | 2.5456 | 0 | 2.1109 | 0.55575 | 0 | 0 | 12.465 | 5.9354 | 8.465 | 0 | 0 | 12.465 | 8.465 | 4.0308 | 4.0308 | 4.0308 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 11 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 12 | 46 | 9 | 12 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 10.95 | 10.95 | 60 | 9.95 | 100% | 0 | 5.8926 | 2.5456 | 0 | 2.1004 | 0.55297 | 0 | 0 | 12.4381 | 5.9226 | 8.4381 | 0 | 0 | 12.4381 | 8.4381 | 4.018 | 4.018 | 4.018 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 12 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 13 | 47 | 9 | 13 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 10.9 | 10.9 | 60 | 9.9 | 100% | 0 | 5.8656 | 2.5456 | 0 | 2.0898 | 0.55019 | 0 | 0 | 12.4112 | 5.9098 | 8.4112 | 0 | 0 | 12.4112 | 8.4112 | 4.0051 | 4.0051 | 4.0051 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 13 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 14 | 48 | 9 | 14 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 9.95 | 9.95 | 60 | 8.95 | 100% | 0 | 5.3544 | 2.5456 | 0 | 1.8893 | 0.4974 | 0 | 0 | 11.9 | 5.6664 | 7.9 | 0 | 0 | 11.9 | 7.9 | 3.7617 | 3.7617 | 3.7617 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 14 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 15 | 49 | 9 | 15 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 8.79 | 8.79 | 60 | 7.79 | 100% | 0 | 4.7302 | 2.5456 | 0 | 1.6444 | 0.43293 | 0 | 0 | 11.2758 | 5.3691 | 7.2758 | 0 | 0 | 11.2758 | 7.2758 | 3.4645 | 3.4645 | 3.4645 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 15 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 16 | 50 | 9 | 16 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 8.95 | 8.95 | 60 | 7.95 | 100% | 0 | 4.8163 | 2.5456 | 0 | 1.6782 | 0.44182 | 0 | 0 | 11.3619 | 5.4101 | 7.3619 | 0 | 0 | 11.3619 | 7.3619 | 3.5055 | 3.5055 | 3.5055 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 16 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 17 | 51 | 9 | 17 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 10.73 | 10.73 | 60 | 9.73 | 100% | 0 | 5.7742 | 2.5456 | 0 | 2.0539 | 0.54074 | 0 | 0 | 12.3198 | 5.8662 | 8.3198 | 0 | 0 | 12.3198 | 8.3198 | 3.9616 | 3.9616 | 3.9616 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 17 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 18 | 52 | 9 | 18 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 33.61 | 33.61 | 60 | 32.61 | 100% | 0 | 18.0867 | 2.5456 | 0 | 6.8837 | 1.8123 | 0 | 0 | 24.6322 | 11.729 | 20.6322 | 0 | 0 | 24.6322 | 20.6322 | 9.8244 | 9.8244 | 9.8244 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 18 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 19 | 53 | 9 | 19 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 82.12 | 82.12 | 60 | 81.12 | 100% | 0 | 44.1915 | 2.5456 | 0 | 17.1238 | 4.5082 | 0 | 0 | 50.7371 | 24.1593 | 46.7371 | 0 | 0 | 50.7371 | 46.7371 | 22.2546 | 22.2546 | 22.2546 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 19 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 20 | 54 | 9 | 20 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 110.5 | 110.5 | 60 | 109.5 | 100% | 0 | 59.4637 | 2.5456 | 0 | 23.1145 | 6.0855 | 0 | 0 | 66.0093 | 31.4314 | 62.0093 | 0 | 0 | 66.0093 | 62.0093 | 29.5267 | 29.5267 | 29.5267 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 20 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 21 | 55 | 9 | 21 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 126.14 | 126.14 | 60 | 125.14 | 100% | 0 | 67.8801 | 2.5456 | 0 | 26.416 | 6.9547 | 0 | 0 | 74.4257 | 35.439 | 70.4257 | 0 | 0 | 74.4257 | 70.4257 | 33.5343 | 33.5343 | 33.5343 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 21 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 22 | 56 | 9 | 22 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 126.44 | 126.44 | 60 | 125.44 | 100% | 0 | 68.0415 | 2.5456 | 0 | 26.4793 | 6.9713 | 0 | 0 | 74.5871 | 35.5159 | 70.5871 | 0 | 0 | 74.5871 | 70.5871 | 33.6112 | 33.6112 | 33.6112 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 22 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 23 | 57 | 9 | 23 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 125.33 | 125.33 | 60 | 124.33 | 100% | 0 | 67.4442 | 2.5456 | 0 | 26.245 | 6.9096 | 0 | 0 | 73.9898 | 35.2314 | 69.9898 | 0 | 0 | 73.9898 | 69.9898 | 33.3268 | 33.3268 | 33.3268 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 23 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
5 | Summer weekend | 24 | 58 | 9 | 24 | 5 | 2 | 40 | 37 | 28 | 6 | 60 | 3 | 63 | 45 | 48 | 63 | 3 | 0.24 | 0.702 | 0 | 3.942 | 3 | 2.1213 | 2.1213 | 2.1213 | 0 | 0 | 0 | 2.1213 | 0.021213 | 2.1001 | 2.1001 | 100% | 1.5832 | 0.53813 | 0 | 0.21109 | 0.055575 | 0 | 0 | 3.1664 | 3.1664 | 2 | 1 | 4 | 0 | 110.79 | 110.79 | 60 | 109.79 | 100% | 0 | 59.6198 | 2.5456 | 0 | 23.1758 | 6.1016 | 0 | 0 | 66.1653 | 31.5057 | 62.1653 | 0 | 0 | 66.1653 | 62.1653 | 29.601 | 29.601 | 29.601 | 55 | 1 | 1 | 0.70711 | 115.5059 | 5 | 24 | Summer weekend | 2 | 6 | 2.1001 | 1.5832 | 0.53813 | 0 | 1.05 | 0.98 | 0.96 | 0.95 | 1.02 | 0.02
6 | Maintenance of HP | 1 | 35 | 10 | 1 | 6 | 0 | 40 | 37 | 28 | 0 | 73.3333 | 3 | 76.3333 | 45 | 48 | 76.3333 | 3 | 0.24 | 0.35533 | 0 | 3.5953 | 3 | 2.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 96.98 | 96.98 | 66 | 95.98 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 1 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 2 | 36 | 10 | 2 | 6 | 0 | 40 | 37 | 28 | 0 | 73.3333 | 3 | 76.3333 | 45 | 48 | 76.3333 | 3 | 0.24 | 0.35533 | 0 | 3.5953 | 3 | 2.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 86.52 | 86.52 | 66 | 85.52 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 2 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 3 | 37 | 10 | 3 | 6 | 0 | 40 | 37 | 28 | 0 | 73.3333 | 3 | 76.3333 | 45 | 48 | 76.3333 | 3 | 0.24 | 0.35533 | 0 | 3.5953 | 3 | 2.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 85.72 | 85.72 | 66 | 84.72 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 3 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 4 | 38 | 10 | 4 | 6 | 0 | 40 | 37 | 28 | 0 | 74.1667 | 3 | 77.1667 | 45 | 48 | 77.1667 | 3 | 0.24 | 0.33367 | 0 | 3.5737 | 3 | 2.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 82.845 | 82.845 | 66 | 81.845 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 4 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 5 | 39 | 10 | 5 | 6 | 0 | 40 | 37 | 28 | 0 | 75 | 3 | 78 | 45 | 48 | 78 | 3 | 0.24 | 0.312 | 0 | 3.552 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 84.63 | 84.63 | 66 | 83.63 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 5 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 6 | 40 | 10 | 6 | 6 | 0 | 40 | 37 | 28 | 0 | 74.1667 | 3 | 77.1667 | 45 | 48 | 77.1667 | 3 | 0.24 | 0.33367 | 0 | 3.5737 | 3 | 2.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 88.5 | 88.5 | 66 | 87.5 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 6 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 7 | 41 | 10 | 7 | 6 | 0 | 40 | 37 | 28 | 0 | 74.1667 | 3 | 77.1667 | 45 | 48 | 77.1667 | 3 | 0.24 | 0.33367 | 0 | 3.5737 | 3 | 2.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 101.015 | 101.015 | 66 | 100.015 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 7 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 8 | 42 | 10 | 8 | 6 | 0 | 40 | 37 | 28 | 0 | 73.3333 | 3 | 76.3333 | 45 | 48 | 76.3333 | 3 | 0.24 | 0.35533 | 0 | 3.5953 | 3 | 2.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 96.625 | 96.625 | 66 | 95.625 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 8 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 9 | 43 | 10 | 9 | 6 | 0 | 40 | 37 | 28 | 0 | 72.5 | 3 | 75.5 | 45 | 48 | 75.5 | 3 | 0.24 | 0.377 | 0 | 3.617 | 3 | 2.8723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 90.64 | 90.64 | 66 | 89.64 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 9 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 10 | 44 | 10 | 10 | 6 | 0 | 40 | 37 | 28 | 0 | 71.6667 | 3 | 74.6667 | 45 | 48 | 74.6667 | 3 | 0.24 | 0.39867 | 0 | 3.6387 | 3 | 2.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 79.405 | 79.405 | 66 | 78.405 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 10 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 11 | 45 | 10 | 11 | 6 | 0 | 40 | 37 | 28 | 0 | 70.8333 | 3 | 73.8333 | 45 | 48 | 73.8333 | 3 | 0.24 | 0.42033 | 0 | 3.6603 | 3 | 2.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 62.495 | 62.495 | 66 | 61.495 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 11 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 12 | 46 | 10 | 12 | 6 | 0 | 40 | 37 | 28 | 0 | 70 | 3 | 73 | 45 | 48 | 73 | 3 | 0.24 | 0.442 | 0 | 3.682 | 3 | 2.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 58.855 | 58.855 | 66 | 57.855 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 12 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 13 | 47 | 10 | 13 | 6 | 0 | 40 | 37 | 28 | 0 | 69.1667 | 3 | 72.1667 | 45 | 48 | 72.1667 | 3 | 0.24 | 0.46367 | 0 | 3.7037 | 3 | 2.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 36.2 | 36.2 | 66 | 35.2 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 13 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 14 | 48 | 10 | 14 | 6 | 0 | 40 | 37 | 28 | 0 | 68.3333 | 3 | 71.3333 | 45 | 48 | 71.3333 | 3 | 0.24 | 0.48533 | 0 | 3.7253 | 3 | 2.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 29.39 | 29.39 | 66 | 28.39 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 14 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 15 | 49 | 10 | 15 | 6 | 0 | 40 | 37 | 28 | 0 | 68.3333 | 3 | 71.3333 | 45 | 48 | 71.3333 | 3 | 0.24 | 0.48533 | 0 | 3.7253 | 3 | 2.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 28.65 | 28.65 | 66 | 27.65 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 15 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 16 | 50 | 10 | 16 | 6 | 0 | 40 | 37 | 28 | 0 | 67.5 | 3 | 70.5 | 45 | 48 | 70.5 | 3 | 0.24 | 0.507 | 0 | 3.747 | 3 | 2.5981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 32.645 | 32.645 | 66 | 31.645 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 16 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 17 | 51 | 10 | 17 | 6 | 0 | 40 | 37 | 28 | 0 | 68.3333 | 3 | 71.3333 | 45 | 48 | 71.3333 | 3 | 0.24 | 0.48533 | 0 | 3.7253 | 3 | 2.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 45.9 | 45.9 | 66 | 44.9 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 17 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 18 | 52 | 10 | 18 | 6 | 0 | 40 | 37 | 28 | 0 | 69.1667 | 3 | 72.1667 | 45 | 48 | 72.1667 | 3 | 0.24 | 0.46367 | 0 | 3.7037 | 3 | 2.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 78.78 | 78.78 | 66 | 77.78 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 18 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 19 | 53 | 10 | 19 | 6 | 0 | 40 | 37 | 28 | 0 | 70 | 3 | 73 | 45 | 48 | 73 | 3 | 0.24 | 0.442 | 0 | 3.682 | 3 | 2.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 94.105 | 94.105 | 66 | 93.105 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 19 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 20 | 54 | 10 | 20 | 6 | 0 | 40 | 37 | 28 | 0 | 70.8333 | 3 | 73.8333 | 45 | 48 | 73.8333 | 3 | 0.24 | 0.42033 | 0 | 3.6603 | 3 | 2.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 116.19 | 116.19 | 66 | 115.19 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 20 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 21 | 55 | 10 | 21 | 6 | 0 | 40 | 37 | 28 | 0 | 71.6667 | 3 | 74.6667 | 45 | 48 | 74.6667 | 3 | 0.24 | 0.39867 | 0 | 3.6387 | 3 | 2.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 153.86 | 153.86 | 66 | 152.86 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 21 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 22 | 56 | 10 | 22 | 6 | 0 | 40 | 37 | 28 | 0 | 72.5 | 3 | 75.5 | 45 | 48 | 75.5 | 3 | 0.24 | 0.377 | 0 | 3.617 | 3 | 2.8723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 116.535 | 116.535 | 66 | 115.535 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 22 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 23 | 57 | 10 | 23 | 6 | 0 | 40 | 37 | 28 | 0 | 72.5 | 3 | 75.5 | 45 | 48 | 75.5 | 3 | 0.24 | 0.377 | 0 | 3.617 | 3 | 2.8723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 109.135 | 109.135 | 66 | 108.135 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 23 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
6 | Maintenance of HP | 24 | 58 | 10 | 24 | 6 | 0 | 40 | 37 | 28 | 0 | 73.3333 | 3 | 76.3333 | 45 | 48 | 76.3333 | 3 | 0.24 | 0.35533 | 0 | 3.5953 | 3 | 2.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 101.005 | 101.005 | 66 | 100.005 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6 | 24 | Maintenance of HP | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 1 | 35 | 11 | 1 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 2 | 36 | 11 | 2 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 3 | 37 | 11 | 3 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 4 | 38 | 11 | 4 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 5 | 39 | 11 | 5 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 6 | 40 | 11 | 6 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 7 | 41 | 11 | 7 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 8 | 42 | 11 | 8 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 9 | 43 | 11 | 9 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 9 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 10 | 44 | 11 | 10 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 10 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 11 | 45 | 11 | 11 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 11 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 12 | 46 | 11 | 12 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 13 | 47 | 11 | 13 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 14 | 48 | 11 | 14 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 15 | 49 | 11 | 15 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 16 | 50 | 11 | 16 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 17 | 51 | 11 | 17 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 18 | 52 | 11 | 18 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 18 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 19 | 53 | 11 | 19 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 20 | 54 | 11 | 20 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 20 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 21 | 55 | 11 | 21 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 22 | 56 | 11 | 22 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 22 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 23 | 57 | 11 | 23 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 23 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
7 | 7 | 24 | 58 | 11 | 24 | 7 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 1 | 35 | 12 | 1 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 2 | 36 | 12 | 2 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 3 | 37 | 12 | 3 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 4 | 38 | 12 | 4 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 5 | 39 | 12 | 5 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 6 | 40 | 12 | 6 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 7 | 41 | 12 | 7 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 8 | 42 | 12 | 8 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 9 | 43 | 12 | 9 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 10 | 44 | 12 | 10 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 11 | 45 | 12 | 11 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 12 | 46 | 12 | 12 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 13 | 47 | 12 | 13 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 13 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 14 | 48 | 12 | 14 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 15 | 49 | 12 | 15 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 16 | 50 | 12 | 16 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 17 | 51 | 12 | 17 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 18 | 52 | 12 | 18 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 18 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 19 | 53 | 12 | 19 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 20 | 54 | 12 | 20 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 21 | 55 | 12 | 21 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 22 | 56 | 12 | 22 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 23 | 57 | 12 | 23 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
8 | 8 | 24 | 58 | 12 | 24 | 8 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 1 | 35 | 13 | 1 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 2 | 36 | 13 | 2 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 3 | 37 | 13 | 3 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 4 | 38 | 13 | 4 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 5 | 39 | 13 | 5 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 6 | 40 | 13 | 6 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 7 | 41 | 13 | 7 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 8 | 42 | 13 | 8 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 9 | 43 | 13 | 9 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 10 | 44 | 13 | 10 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 11 | 45 | 13 | 11 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 11 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 12 | 46 | 13 | 12 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 12 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 13 | 47 | 13 | 13 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 13 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 14 | 48 | 13 | 14 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 14 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 15 | 49 | 13 | 15 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 15 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 16 | 50 | 13 | 16 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 17 | 51 | 13 | 17 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 17 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 18 | 52 | 13 | 18 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 18 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 19 | 53 | 13 | 19 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 19 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 20 | 54 | 13 | 20 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 21 | 55 | 13 | 21 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 21 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 22 | 56 | 13 | 22 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 22 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 23 | 57 | 13 | 23 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 23 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
9 | 9 | 24 | 58 | 13 | 24 | 9 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 24 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 1 | 35 | 14 | 1 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 2 | 36 | 14 | 2 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 3 | 37 | 14 | 3 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 4 | 38 | 14 | 4 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 5 | 39 | 14 | 5 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 6 | 40 | 14 | 6 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 7 | 41 | 14 | 7 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 8 | 42 | 14 | 8 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 9 | 43 | 14 | 9 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 10 | 44 | 14 | 10 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 11 | 45 | 14 | 11 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 12 | 46 | 14 | 12 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 13 | 47 | 14 | 13 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 14 | 48 | 14 | 14 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 15 | 49 | 14 | 15 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 16 | 50 | 14 | 16 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 17 | 51 | 14 | 17 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 18 | 52 | 14 | 18 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 19 | 53 | 14 | 19 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 20 | 54 | 14 | 20 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 21 | 55 | 14 | 21 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 22 | 56 | 14 | 22 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 23 | 57 | 14 | 23 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
10 | 10 | 24 | 58 | 14 | 24 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 1 | 35 | 15 | 1 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 2 | 36 | 15 | 2 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 3 | 37 | 15 | 3 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 4 | 38 | 15 | 4 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 4 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 5 | 39 | 15 | 5 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 6 | 40 | 15 | 6 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 7 | 41 | 15 | 7 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 7 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 8 | 42 | 15 | 8 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 9 | 43 | 15 | 9 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 9 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 10 | 44 | 15 | 10 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 11 | 45 | 15 | 11 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 12 | 46 | 15 | 12 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 12 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 13 | 47 | 15 | 13 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 14 | 48 | 15 | 14 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 15 | 49 | 15 | 15 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 16 | 50 | 15 | 16 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 17 | 51 | 15 | 17 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 18 | 52 | 15 | 18 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 18 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 19 | 53 | 15 | 19 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 19 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 20 | 54 | 15 | 20 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 20 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 21 | 55 | 15 | 21 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 21 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 22 | 56 | 15 | 22 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 23 | 57 | 15 | 23 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
11 | 11 | 24 | 58 | 15 | 24 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 1 | 35 | 16 | 1 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 2 | 36 | 16 | 2 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 3 | 37 | 16 | 3 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 4 | 38 | 16 | 4 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 5 | 39 | 16 | 5 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 6 | 40 | 16 | 6 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 7 | 41 | 16 | 7 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 7 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 8 | 42 | 16 | 8 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 9 | 43 | 16 | 9 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 9 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 10 | 44 | 16 | 10 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 11 | 45 | 16 | 11 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 11 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 12 | 46 | 16 | 12 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 13 | 47 | 16 | 13 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 13 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 14 | 48 | 16 | 14 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 15 | 49 | 16 | 15 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 16 | 50 | 16 | 16 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 17 | 51 | 16 | 17 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 18 | 52 | 16 | 18 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 19 | 53 | 16 | 19 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 20 | 54 | 16 | 20 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 21 | 55 | 16 | 21 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 22 | 56 | 16 | 22 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 23 | 57 | 16 | 23 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 23 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
12 | 12 | 24 | 58 | 16 | 24 | 12 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 1 | 35 | 17 | 1 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 2 | 36 | 17 | 2 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 3 | 37 | 17 | 3 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 4 | 38 | 17 | 4 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 5 | 39 | 17 | 5 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 6 | 40 | 17 | 6 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 6 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 7 | 41 | 17 | 7 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 7 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 8 | 42 | 17 | 8 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 8 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 9 | 43 | 17 | 9 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 9 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 10 | 44 | 17 | 10 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 11 | 45 | 17 | 11 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 11 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 12 | 46 | 17 | 12 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 12 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 13 | 47 | 17 | 13 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 14 | 48 | 17 | 14 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 14 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 15 | 49 | 17 | 15 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 16 | 50 | 17 | 16 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 17 | 51 | 17 | 17 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 17 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 18 | 52 | 17 | 18 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 18 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 19 | 53 | 17 | 19 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 19 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 20 | 54 | 17 | 20 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 21 | 55 | 17 | 21 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 22 | 56 | 17 | 22 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 23 | 57 | 17 | 23 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 23 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
13 | 13 | 24 | 58 | 17 | 24 | 13 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 1 | 35 | 18 | 1 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 2 | 36 | 18 | 2 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 3 | 37 | 18 | 3 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 4 | 38 | 18 | 4 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 5 | 39 | 18 | 5 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 6 | 40 | 18 | 6 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 7 | 41 | 18 | 7 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 7 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 8 | 42 | 18 | 8 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 9 | 43 | 18 | 9 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 10 | 44 | 18 | 10 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 11 | 45 | 18 | 11 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 11 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 12 | 46 | 18 | 12 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 13 | 47 | 18 | 13 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 14 | 48 | 18 | 14 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 15 | 49 | 18 | 15 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 16 | 50 | 18 | 16 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 17 | 51 | 18 | 17 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 18 | 52 | 18 | 18 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 18 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 19 | 53 | 18 | 19 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 20 | 54 | 18 | 20 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 21 | 55 | 18 | 21 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 22 | 56 | 18 | 22 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 23 | 57 | 18 | 23 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
14 | 14 | 24 | 58 | 18 | 24 | 14 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 1 | 35 | 19 | 1 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 2 | 36 | 19 | 2 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 3 | 37 | 19 | 3 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 4 | 38 | 19 | 4 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 5 | 39 | 19 | 5 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 6 | 40 | 19 | 6 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 7 | 41 | 19 | 7 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 8 | 42 | 19 | 8 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 9 | 43 | 19 | 9 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 10 | 44 | 19 | 10 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 11 | 45 | 19 | 11 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 12 | 46 | 19 | 12 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 13 | 47 | 19 | 13 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 14 | 48 | 19 | 14 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 15 | 49 | 19 | 15 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 16 | 50 | 19 | 16 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 17 | 51 | 19 | 17 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 18 | 52 | 19 | 18 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 19 | 53 | 19 | 19 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 20 | 54 | 19 | 20 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 21 | 55 | 19 | 21 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 22 | 56 | 19 | 22 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 23 | 57 | 19 | 23 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
15 | 15 | 24 | 58 | 19 | 24 | 15 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 1 | 35 | 20 | 1 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 2 | 36 | 20 | 2 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 3 | 37 | 20 | 3 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 4 | 38 | 20 | 4 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 5 | 39 | 20 | 5 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 6 | 40 | 20 | 6 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 7 | 41 | 20 | 7 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 8 | 42 | 20 | 8 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 9 | 43 | 20 | 9 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 10 | 44 | 20 | 10 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 11 | 45 | 20 | 11 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 12 | 46 | 20 | 12 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 13 | 47 | 20 | 13 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 14 | 48 | 20 | 14 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 15 | 49 | 20 | 15 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 16 | 50 | 20 | 16 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 17 | 51 | 20 | 17 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 18 | 52 | 20 | 18 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 19 | 53 | 20 | 19 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 20 | 54 | 20 | 20 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 21 | 55 | 20 | 21 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 22 | 56 | 20 | 22 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 23 | 57 | 20 | 23 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
16 | 16 | 24 | 58 | 20 | 24 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 1 | 35 | 21 | 1 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 2 | 36 | 21 | 2 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 3 | 37 | 21 | 3 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 4 | 38 | 21 | 4 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 5 | 39 | 21 | 5 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 6 | 40 | 21 | 6 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 7 | 41 | 21 | 7 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 8 | 42 | 21 | 8 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 9 | 43 | 21 | 9 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 10 | 44 | 21 | 10 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 11 | 45 | 21 | 11 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 12 | 46 | 21 | 12 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 13 | 47 | 21 | 13 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 14 | 48 | 21 | 14 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 15 | 49 | 21 | 15 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 16 | 50 | 21 | 16 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 17 | 51 | 21 | 17 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 18 | 52 | 21 | 18 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 19 | 53 | 21 | 19 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 20 | 54 | 21 | 20 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 21 | 55 | 21 | 21 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 22 | 56 | 21 | 22 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 23 | 57 | 21 | 23 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 23 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
17 | 17 | 24 | 58 | 21 | 24 | 17 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 1 | 35 | 22 | 1 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 2 | 36 | 22 | 2 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 3 | 37 | 22 | 3 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 4 | 38 | 22 | 4 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 5 | 39 | 22 | 5 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 6 | 40 | 22 | 6 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 7 | 41 | 22 | 7 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 8 | 42 | 22 | 8 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 9 | 43 | 22 | 9 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 10 | 44 | 22 | 10 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 11 | 45 | 22 | 11 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 12 | 46 | 22 | 12 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 13 | 47 | 22 | 13 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 14 | 48 | 22 | 14 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 15 | 49 | 22 | 15 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 16 | 50 | 22 | 16 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 17 | 51 | 22 | 17 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 18 | 52 | 22 | 18 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 19 | 53 | 22 | 19 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 20 | 54 | 22 | 20 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 21 | 55 | 22 | 21 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 22 | 56 | 22 | 22 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 23 | 57 | 22 | 23 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 23 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
18 | 18 | 24 | 58 | 22 | 24 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 24 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 1 | 35 | 23 | 1 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 2 | 36 | 23 | 2 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 3 | 37 | 23 | 3 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 4 | 38 | 23 | 4 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 5 | 39 | 23 | 5 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 6 | 40 | 23 | 6 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 7 | 41 | 23 | 7 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 8 | 42 | 23 | 8 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 9 | 43 | 23 | 9 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 10 | 44 | 23 | 10 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 11 | 45 | 23 | 11 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 12 | 46 | 23 | 12 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 13 | 47 | 23 | 13 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 14 | 48 | 23 | 14 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 14 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 15 | 49 | 23 | 15 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 16 | 50 | 23 | 16 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 17 | 51 | 23 | 17 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 18 | 52 | 23 | 18 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 19 | 53 | 23 | 19 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 20 | 54 | 23 | 20 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 21 | 55 | 23 | 21 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 22 | 56 | 23 | 22 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 23 | 57 | 23 | 23 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
19 | 19 | 24 | 58 | 23 | 24 | 19 | 0 | 0 | 0 | 28 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 3 | -0.5 | 2.262 | 0 | 4.762 | 3 | 0.54772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 11 | 11 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 24 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 0.02 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 1 | 35 | 24 | 1 | 20 | 0.001 | 30 | 27 | 28 | 100 | 93 | 3 | 96 | 45 | 48 | 95 | 3 | 0.04 | -0.13 | 0 | 2.91 | 3 | 3 | 0.0015236 | 0.0015236 | 1 | 3.2416e-05 | 3.2416e-05 | 0.001556 | 1.556e-05 | 0.0015404 | 0.0015404 | 100% | 0.001 | 0.00052356 | 3.2744e-05 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 77 | 77 | 0 | 100 | 100% | 0 | 0.040314 | 0 | 0.0025213 | 0 | 0.013333 | 0 | 0 | 0.044835 | 29.106 | 0.042835 | 0 | 0 | 0.044835 | 0.042835 | 27.8077 | 27.8077 | 27.8077 | 65 | 0 | 0 | 0 | 0.10013 | 20 | 1 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 2 | 36 | 24 | 2 | 20 | 0.001 | 30 | 27 | 28 | 100 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.04 | 0.0086667 | 0 | 3.0487 | 3 | 3 | 0.0014881 | 0.0014881 | 0 | 0 | 0 | 0.0014881 | 1.4881e-05 | 0.0014732 | 0.0014732 | 100% | 0.001 | 0.00048812 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 74.45 | 74.45 | 0 | 100 | 100% | 0 | 0.036341 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.038341 | 26.0247 | 0.036341 | 0 | 0 | 0.038341 | 0.036341 | 24.6672 | 24.6672 | 24.6672 | 65 | 0 | 0 | 0 | 0.095761 | 20 | 2 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 3 | 37 | 24 | 3 | 20 | 0.001 | 30 | 27 | 28 | 100 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.04 | 0.0086667 | 0 | 3.0487 | 3 | 3 | 0.0014881 | 0.0014881 | 0 | 0 | 0 | 0.0014881 | 1.4881e-05 | 0.0014732 | 0.0014732 | 100% | 0.001 | 0.00048812 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 74.54 | 74.54 | 0 | 100 | 100% | 0 | 0.036385 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.038385 | 26.0546 | 0.036385 | 0 | 0 | 0.038385 | 0.036385 | 24.697 | 24.697 | 24.697 | 65 | 0 | 0 | 0 | 0.095761 | 20 | 3 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 4 | 38 | 24 | 4 | 20 | 0.001 | 30 | 27 | 28 | 100 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.04 | -0.034667 | 0 | 3.0053 | 3 | 3 | 0.0014987 | 0.0014987 | 0 | 0 | 0 | 0.0014987 | 1.4987e-05 | 0.0014837 | 0.0014837 | 100% | 0.001 | 0.00049867 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 72.82 | 72.82 | 0 | 100 | 100% | 0 | 0.036313 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.038313 | 25.823 | 0.036313 | 0 | 0 | 0.038313 | 0.036313 | 24.475 | 24.475 | 24.475 | 65 | 0 | 0 | 0 | 0.096439 | 20 | 4 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 5 | 39 | 24 | 5 | 20 | 0.001 | 30 | 27 | 28 | 100 | 88 | 3 | 91 | 45 | 48 | 91 | 3 | 0.04 | -0.026 | 0 | 3.014 | 3 | 3 | 0.0014965 | 0.0014965 | 0 | 0 | 0 | 0.0014965 | 1.4965e-05 | 0.0014816 | 0.0014816 | 100% | 0.001 | 0.00049652 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 72.85 | 72.85 | 0 | 100 | 100% | 0 | 0.036172 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.038172 | 25.7646 | 0.036172 | 0 | 0 | 0.038172 | 0.036172 | 24.4147 | 24.4147 | 24.4147 | 65 | 0 | 0 | 0 | 0.096301 | 20 | 5 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 6 | 40 | 24 | 6 | 20 | 0.001 | 30 | 27 | 28 | 100 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.04 | -0.034667 | 0 | 3.0053 | 3 | 3 | 0.0014987 | 0.0014987 | 0 | 0 | 0 | 0.0014987 | 1.4987e-05 | 0.0014837 | 0.0014837 | 100% | 0.001 | 0.00049867 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 72.75 | 72.75 | 0 | 100 | 100% | 0 | 0.036278 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.038278 | 25.7995 | 0.036278 | 0 | 0 | 0.038278 | 0.036278 | 24.4515 | 24.4515 | 24.4515 | 65 | 0 | 0 | 0 | 0.096439 | 20 | 6 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 7 | 41 | 24 | 7 | 20 | 0.001 | 30 | 27 | 28 | 100 | 88.3333 | 3 | 91.3333 | 45 | 48 | 91.3333 | 3 | 0.04 | -0.034667 | 0 | 3.0053 | 3 | 3 | 0.0014987 | 0.0014987 | 0 | 0 | 0 | 0.0014987 | 1.4987e-05 | 0.0014837 | 0.0014837 | 100% | 0.001 | 0.00049867 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 73.59 | 73.59 | 0 | 100 | 100% | 0 | 0.036697 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.038697 | 26.0818 | 0.036697 | 0 | 0 | 0.038697 | 0.036697 | 24.7338 | 24.7338 | 24.7338 | 65 | 0 | 0 | 0 | 0.096439 | 20 | 7 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 8 | 42 | 24 | 8 | 20 | 0.001 | 30 | 27 | 28 | 100 | 86.6667 | 3 | 89.6667 | 45 | 48 | 89.6667 | 3 | 0.04 | 0.0086667 | 0 | 3.0487 | 3 | 3 | 0.0014881 | 0.0014881 | 0 | 0 | 0 | 0.0014881 | 1.4881e-05 | 0.0014732 | 0.0014732 | 100% | 0.001 | 0.00048812 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 77.9 | 77.9 | 0 | 100 | 100% | 0 | 0.038025 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.040025 | 27.1678 | 0.038025 | 0 | 0 | 0.040025 | 0.038025 | 25.8103 | 25.8103 | 25.8103 | 65 | 0 | 0 | 0 | 0.095761 | 20 | 8 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 9 | 43 | 24 | 9 | 20 | 0.001 | 30 | 27 | 28 | 100 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.04 | 0.052 | 0 | 3.092 | 3 | 3 | 0.001478 | 0.001478 | 0 | 0 | 0 | 0.001478 | 1.478e-05 | 0.0014632 | 0.0014632 | 100% | 0.001 | 0.00047801 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 85.82 | 85.82 | 0 | 100 | 100% | 0 | 0.041023 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.043023 | 29.4027 | 0.041023 | 0 | 0 | 0.043023 | 0.041023 | 28.0359 | 28.0359 | 28.0359 | 65 | 0 | 0 | 0 | 0.09511 | 20 | 9 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 10 | 44 | 24 | 10 | 20 | 0.001 | 30 | 27 | 28 | 100 | 83.3333 | 3 | 86.3333 | 45 | 48 | 86.3333 | 3 | 0.04 | 0.095333 | 0 | 3.1353 | 3 | 3 | 0.0014683 | 0.0014683 | 0 | 0 | 0 | 0.0014683 | 1.4683e-05 | 0.0014536 | 0.0014536 | 100% | 0.001 | 0.00046831 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 88.9 | 88.9 | 0 | 100 | 100% | 0 | 0.041633 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.043633 | 30.0165 | 0.041633 | 0 | 0 | 0.043633 | 0.041633 | 28.6406 | 28.6406 | 28.6406 | 65 | 0 | 0 | 0 | 0.094486 | 20 | 10 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 11 | 45 | 24 | 11 | 20 | 0.001 | 30 | 27 | 28 | 100 | 81.6667 | 3 | 84.6667 | 45 | 48 | 84.6667 | 3 | 0.04 | 0.13867 | 0 | 3.1787 | 3 | 3 | 0.001459 | 0.001459 | 0 | 0 | 0 | 0.001459 | 1.459e-05 | 0.0014444 | 0.0014444 | 100% | 0.001 | 0.000459 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 82.8 | 82.8 | 0 | 100 | 100% | 0 | 0.038005 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.040005 | 27.6964 | 0.038005 | 0 | 0 | 0.040005 | 0.038005 | 26.3118 | 26.3118 | 26.3118 | 65 | 0 | 0 | 0 | 0.093886 | 20 | 11 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 12 | 46 | 24 | 12 | 20 | 0.001 | 30 | 27 | 28 | 100 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.04 | 0.182 | 0 | 3.222 | 3 | 3 | 0.00145 | 0.00145 | 0 | 0 | 0 | 0.00145 | 1.45e-05 | 0.0014355 | 0.0014355 | 100% | 0.001 | 0.00045005 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 81.77 | 81.77 | 0 | 100 | 100% | 0 | 0.0368 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.0388 | 27.0282 | 0.0368 | 0 | 0 | 0.0388 | 0.0368 | 25.635 | 25.635 | 25.635 | 65 | 0 | 0 | 0 | 0.09331 | 20 | 12 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 13 | 47 | 24 | 13 | 20 | 0.001 | 30 | 27 | 28 | 100 | 78.3333 | 3 | 81.3333 | 45 | 48 | 81.3333 | 3 | 0.04 | 0.22533 | 0 | 3.2653 | 3 | 3 | 0.0014414 | 0.0014414 | 0 | 0 | 0 | 0.0014414 | 1.4414e-05 | 0.001427 | 0.001427 | 100% | 0.001 | 0.00044144 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 78.73 | 78.73 | 0 | 100 | 100% | 0 | 0.034754 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.036754 | 25.7559 | 0.034754 | 0 | 0 | 0.036754 | 0.034754 | 24.3544 | 24.3544 | 24.3544 | 65 | 0 | 0 | 0 | 0.092756 | 20 | 13 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 14 | 48 | 24 | 14 | 20 | 0.001 | 30 | 27 | 28 | 100 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.04 | 0.26867 | 0 | 3.3087 | 3 | 3 | 0.0014332 | 0.0014332 | 0 | 0 | 0 | 0.0014332 | 1.4332e-05 | 0.0014188 | 0.0014188 | 100% | 0.001 | 0.00043315 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 79.78 | 79.78 | 0 | 100 | 100% | 0 | 0.034557 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.036557 | 25.7656 | 0.034557 | 0 | 0 | 0.036557 | 0.034557 | 24.356 | 24.356 | 24.356 | 65 | 0 | 0 | 0 | 0.092223 | 20 | 14 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 15 | 49 | 24 | 15 | 20 | 0.001 | 30 | 27 | 28 | 100 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.04 | 0.26867 | 0 | 3.3087 | 3 | 3 | 0.0014332 | 0.0014332 | 0 | 0 | 0 | 0.0014332 | 1.4332e-05 | 0.0014188 | 0.0014188 | 100% | 0.001 | 0.00043315 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 84.39 | 84.39 | 0 | 100 | 100% | 0 | 0.036554 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.038554 | 27.173 | 0.036554 | 0 | 0 | 0.038554 | 0.036554 | 25.7634 | 25.7634 | 25.7634 | 65 | 0 | 0 | 0 | 0.092223 | 20 | 15 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 16 | 50 | 24 | 16 | 20 | 0.001 | 30 | 27 | 28 | 100 | 75 | 3 | 78 | 45 | 48 | 78 | 3 | 0.04 | 0.312 | 0 | 3.352 | 3 | 3 | 0.0014252 | 0.0014252 | 0 | 0 | 0 | 0.0014252 | 1.4252e-05 | 0.0014109 | 0.0014109 | 100% | 0.001 | 0.00042517 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 90.11 | 90.11 | 0 | 100 | 100% | 0 | 0.038312 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.040312 | 28.5715 | 0.038312 | 0 | 0 | 0.040312 | 0.038312 | 27.154 | 27.154 | 27.154 | 65 | 0 | 0 | 0 | 0.09171 | 20 | 16 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 17 | 51 | 24 | 17 | 20 | 0.001 | 30 | 27 | 28 | 100 | 76.6667 | 3 | 79.6667 | 45 | 48 | 79.6667 | 3 | 0.04 | 0.26867 | 0 | 3.3087 | 3 | 3 | 0.0014332 | 0.0014332 | 0 | 0 | 0 | 0.0014332 | 1.4332e-05 | 0.0014188 | 0.0014188 | 100% | 0.001 | 0.00043315 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 98.8 | 98.8 | 0 | 100 | 100% | 0 | 0.042795 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.044795 | 31.5722 | 0.042795 | 0 | 0 | 0.044795 | 0.042795 | 30.1626 | 30.1626 | 30.1626 | 65 | 0 | 0 | 0 | 0.092223 | 20 | 17 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 18 | 52 | 24 | 18 | 20 | 0.001 | 30 | 27 | 28 | 100 | 78.3333 | 3 | 81.3333 | 45 | 48 | 81.3333 | 3 | 0.04 | 0.22533 | 0 | 3.2653 | 3 | 3 | 0.0014414 | 0.0014414 | 0 | 0 | 0 | 0.0014414 | 1.4414e-05 | 0.001427 | 0.001427 | 100% | 0.001 | 0.00044144 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 105.93 | 105.93 | 0 | 100 | 100% | 0 | 0.046761 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.048761 | 34.17 | 0.046761 | 0 | 0 | 0.048761 | 0.046761 | 32.7685 | 32.7685 | 32.7685 | 65 | 0 | 0 | 0 | 0.092756 | 20 | 18 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 19 | 53 | 24 | 19 | 20 | 0.001 | 30 | 27 | 28 | 100 | 80 | 3 | 83 | 45 | 48 | 83 | 3 | 0.04 | 0.182 | 0 | 3.222 | 3 | 3 | 0.00145 | 0.00145 | 0 | 0 | 0 | 0.00145 | 1.45e-05 | 0.0014355 | 0.0014355 | 100% | 0.001 | 0.00045005 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 110.87 | 110.87 | 0 | 100 | 100% | 0 | 0.049896 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.051896 | 36.1511 | 0.049896 | 0 | 0 | 0.051896 | 0.049896 | 34.7579 | 34.7579 | 34.7579 | 65 | 0 | 0 | 0 | 0.09331 | 20 | 19 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 20 | 54 | 24 | 20 | 20 | 0.001 | 30 | 27 | 28 | 100 | 81.6667 | 3 | 84.6667 | 45 | 48 | 84.6667 | 3 | 0.04 | 0.13867 | 0 | 3.1787 | 3 | 3 | 0.001459 | 0.001459 | 0 | 0 | 0 | 0.001459 | 1.459e-05 | 0.0014444 | 0.0014444 | 100% | 0.001 | 0.000459 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 102.57 | 102.57 | 0 | 100 | 100% | 0 | 0.047079 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.049079 | 33.9788 | 0.047079 | 0 | 0 | 0.049079 | 0.047079 | 32.5942 | 32.5942 | 32.5942 | 65 | 0 | 0 | 0 | 0.093886 | 20 | 20 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 21 | 55 | 24 | 21 | 20 | 0.001 | 30 | 27 | 28 | 100 | 83.3333 | 3 | 86.3333 | 45 | 48 | 86.3333 | 3 | 0.04 | 0.095333 | 0 | 3.1353 | 3 | 3 | 0.0014683 | 0.0014683 | 0 | 0 | 0 | 0.0014683 | 1.4683e-05 | 0.0014536 | 0.0014536 | 100% | 0.001 | 0.00046831 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 92.97 | 92.97 | 0 | 100 | 100% | 0 | 0.043539 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.045539 | 31.3277 | 0.043539 | 0 | 0 | 0.045539 | 0.043539 | 29.9519 | 29.9519 | 29.9519 | 65 | 0 | 0 | 0 | 0.094486 | 20 | 21 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 22 | 56 | 24 | 22 | 20 | 0.001 | 30 | 27 | 28 | 100 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.04 | 0.052 | 0 | 3.092 | 3 | 3 | 0.001478 | 0.001478 | 0 | 0 | 0 | 0.001478 | 1.478e-05 | 0.0014632 | 0.0014632 | 100% | 0.001 | 0.00047801 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 86.74 | 86.74 | 0 | 100 | 100% | 0 | 0.041463 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.043463 | 29.7032 | 0.041463 | 0 | 0 | 0.043463 | 0.041463 | 28.3364 | 28.3364 | 28.3364 | 65 | 0 | 0 | 0 | 0.09511 | 20 | 22 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 23 | 57 | 24 | 23 | 20 | 0.001 | 30 | 27 | 28 | 100 | 85 | 3 | 88 | 45 | 48 | 88 | 3 | 0.04 | 0.052 | 0 | 3.092 | 3 | 3 | 0.001478 | 0.001478 | 0 | 0 | 0 | 0.001478 | 1.478e-05 | 0.0014632 | 0.0014632 | 100% | 0.001 | 0.00047801 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 85.68 | 85.68 | 0 | 100 | 100% | 0 | 0.040956 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.042956 | 29.357 | 0.040956 | 0 | 0 | 0.042956 | 0.040956 | 27.9901 | 27.9901 | 27.9901 | 65 | 0 | 0 | 0 | 0.09511 | 20 | 23 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
20 | 20 | 24 | 58 | 24 | 24 | 20 | 0.001 | 30 | 27 | 28 | 100 | 86.6667 | 3 | 89.6667 | 0 | 3 | 89.6667 | 3 | 0.04 | 0.0086667 | 0 | 3.0487 | 3 | 3 | 0.0014881 | 0.0014881 | 0 | 0 | 0 | 0.0014881 | 1.4881e-05 | 0.0014732 | 0.0014732 | 100% | 0.001 | 0.00048812 | 0 | 0 | 0.00013333 | 0 | 0 | 0.002 | 0.002 | 2 | 1 | 0.002 | 0 | 80.13 | 80.13 | 0 | 100 | 100% | 0 | 0.039113 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 0.041113 | 27.9067 | 0.039113 | 0 | 0 | 0.041113 | 0.039113 | 26.5491 | 26.5491 | 26.5491 | 65 | 0 | 0 | 0 | 0.095761 | 20 | 24 | 20 | 0.001 | 100 | 0 | 0 | 0 | 0 | 1.05 | 0.98 | -0.025 | 0.95 | 0.03 | 0.02
Typical Day ID |  | Hour | 0 | 0 | 0 | 0 | Available waste heat (DC heat source) | Flow temperature of data centre cooling system | Flow Temperature HP | Return temperature HP / Flow temperature DC | Max heat demand - grid (HP heat sink) | DH supply line temperature | Delta T DH / Heat pump | Required temperature sink out | DH return line temperature | Temperature heat pump sink in | Actual Heat pump Temperature Sink Out | Nominal COP | COP increase due to higher heat source temperature | COP increase due to lower heat sink out temperature (eg. DH supply line temperature) | COP increase due to higher heat sink in temperature (eg. DH return line temperature) | COP at current operation conditions | Nominal capacity of heat pump | Reduced capacity of heat pump due to volume restrictions | Potential heat output - HP, including heat losses, not considering | HP output due to Booster Capacity restrictions | Delta T Booster | Required Booster heat output | Booster heat output | Total heat output before additional losses | Heat losses after HP | Total heat output after additional losses | Total heat output after considering restriction imposed by heat demand | Share of heat provided by heat pump and booster utilized by grid | Waste heat input from DC | Electricity input for heat pump | Energy input for booster | Avoided electricity demand due to reduced active cooling | Remaining electricity demand for active cooling | Waste heat price p_0 that is paid at the border between data centre cooling and waste heat recovery system under Take-or-Pay conditions | Energy costs p_0 for waste heat from DC | Variable O&M costs for heat recovery system operator | Total Hourly costs of heat recovery system operator | Negotiated Waste heat price p_1 | Contract type for waste heat between Contractor 1 / DH operator and Contractor 2 / data centre operator | Energy costs p_1 for waste heat from DC as provided by DC (take-or-pay) (Contractor 1) | Energy costs p_1 for waste heat from DC as taken (Pay-as-you-go) (Contractor 1) | Electricity price Heat pump | Fuel price booster | Electricity price auxiliary energy | Data centre operator: Electricity price for cooling unit | Data centre operator: Share of active cooling needed if heat is not taken up by DH | Average Subsidies given Contractor 1 per utilized waste heat | Electricity costs for heat pump (Contractor 1) | Electricity costs auxiliary energy (Contractor 1) | Fuel costs for booster (Contractor 1) | Avoided electricity costs due to reduced active cooling | Remaining electricity costs for active cooling | Subsidies given per utilized waste heat to Contractor 1 / DH Operator | Subsidies given per utilized waste heat to Contractor 1 / DH Operator considering that they must not exceed costs for electricity | Total energy costs considering subsidies Contractor 1 / DH operator including subsidies S3 provided for the utilized waste heat | Total energy costs per delivered Heat to Grid Contractor 1 / DH Operator | Total SRMC energy costs Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Variable (MWh-specific) O&M Costs Heat pump Contractor 1 / DH Operator | Variable (MWh-specific) O&M Costs Booster Contractor 1 / DH Operator | Total Hourly costs of Contractor 1 / DH Operator including subsidies S3 provided for the utilized waste heat | Short run marginal costs per hour Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator excluding subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator including subsidies S3 provided for the utilized waste heat | Short run marginal costs per MWh Contractor 1 / DH Operator used to compare against reference SRMC alternative production | Reference SRMC alternative production [EUR/MWh_delivered] | Is Heat production because SRMC lower than alternative, temperature can be met and system is available | Operation hours | Operation hours in full-load-hours equivalents | Reference SRMC alternative production [EUR/h] | Typical Day ID | Hour | Name of typical day | Waste heat output DC | Max heat demand grid | Heat fed into grid considering actual operation | Waste heat input from DC actual operation | Electricity input for heat pump actual operation | Energy input for booster actual operation
CHECK Total sum if System is running |  | 1479 | 5525 | 832 | 1479 | 356 | 238 | 4760 | 4403 | 3332 | 714 | 8788.3333 | 357 | 9145.3333 | 5355 | 5712 | 9137.3333 | 357 | 28.56 | 40.8893 | 0 | 426.4493 | 357 | 315.7021 | 305.1732 | 305.1732 | 8 | 0.50176 | 0.50176 | 305.675 | 3.0568 | 302.6183 | 302.6183 | 119 | 218.4098 | 86.7634 | 0.50683 | 21.228 | 2.612 | 0 | 0 | 436.8196 | 436.8196 | 238 | 119 | 476 | 0 | 9460.86 | 9460.86 | 9468 | 9341.86 | 89.4 | 0 | 6962.4755 | 500.2699 | 38.8386 | 1636.6382 | 196.864 | 0 | 0 | 7977.5841 | 3088.6502 | 7501.5841 | 0 | 0 | 7977.5841 | 7501.5841 | 2897.386 | 2897.386 | 2897.386 | 6680 | 119 | 119 | 101.7244 | 17279.91 | 356 | 1479 | 0 | 238 | 714 | 302.6183 | 218.4098 | 86.7634 | 0.50683
CHECK Total sum |  | 6000 | 22320 | 6960 | 6000 | 5040 | 240.024 | 6480 | 5976 | 13440 | 3120 | 12565.1667 | 1440 | 14005.1667 | 7515 | 8955 | 13996.1667 | 1440 | -120.48 | 759.2997 | 0 | 2078.8197 | 1440 | 628.4035 | 307.3298 | 307.3298 | 9 | 0.5018 | 0.5018 | 307.8316 | 3.0783 | 304.7533 | 304.7533 | 480 | 220.017 | 87.3128 | 0.50687 | 21.228 | 2.8819 | 0 | 0 | 440.034 | 440.034 | 960 | 480 | 480.048 | 0 | 17082.835 | 17082.835 | 11112 | 13874.945 | 138.4 | 0 | 7071.8376 | 502.8155 | 38.8411 | 1636.6382 | 250.64 | 0 | 0 | 8093.5422 | 3830.7879 | 7613.4942 | 0 | 0 | 8093.5422 | 7613.4942 | 3604.6392 | 3604.6392 | 3604.6392 | 9600 | 119 | 119 | 101.7244 | 17366.1857 | 5040 | 6000 | 4056 | 240.024 | 3120 | 302.6183 | 218.4098 | 86.7634 | 0.50683

## Calculation of Typical Year
Go to Content
Colour Code | Header
Item / unit
User input
Cell with formula
Go to content
Input - not used for calculation
Not used anymore: relevant for future works - do not change
Control cells
| Check settings / input data, there might be some error | [37 empty] | Go to Main Results
[39 empty] | Contractor 1 / District Heating Operator | [5 empty] | Economic parameter waste heat recovery system | [7 empty] | Contractor 2 / Data centre operator
Energy-related and economic parameters Contractor 1 / District heating operator
| Typical days | Name of typical day | Days of Typical Day in Typical Year | Available heat from DC per day | Used heat from DC per day | Hours of operation per day | Hours of operation (Full-load-hours equivalents) per day | Heat provided to the grid on a typical day | Electricity used by Heat pump per day | Electricity / fuel used by booster per day | Waste heat costs per day based on negotiated price p_1 between Contractor 1 / DH Operator and Contractor 2 / DC Operator | Electricity costs HP per day | Electricity costs auxiliary energy per day | Fuel costs Booster per day | Variable O&M costs HP per day | Variable O&M costs Booster per day | Total variable costs excluding subsidies per day | Avoided variable costs (SRMC) of alternative production per day | Subsidies for utilized waste heat provided by DC per day | Waste heat costs per day for Take-or-pay contract (NOT part of SRMC) | Hours of operation per year | Hours of operation (Full-load-hours equivalents) per year | Available heat from DC per year | Used heat from DC per year | Heat provided into the grid per year | Electricity used by Heat pump per year | Electricity / fuel used by booster per year | Waste heat costs per year for Pay-as-you-go contract (part of SRMC) | Electricity cost HP per year | Electricity costs auxiliary energy per year | Fuel costs Booster per year | Variable O&M costs HP per year | Variable O&M costs Booster per year | Variable costs excluding subsidies per year | Avoided variable costs (SRMC) of alternative production per year | Subsidies (earnings) for utilized waste heat provided by DC per year | Waste heat costs per year for Take-or-pay contract (NOT part of SRMC) |  | Total investment |  |  | Annual operation independent O&M expenses |  |  | Total investment |  |  | Share paid by Contractor 1 | Annual operation independent O&M expenses |  |  | Share paid by Contractor 1 | Total investment |  |  | Annual operation independent O&M expenses
| - |  | days | MWh_th/day | MWh_th/day | hours/day | hours/day | MWh_th/day | MWh_el/day | MWh_input/day | EUR/day | EUR/day | EUR / day | EUR / day | EUR / day | EUR / day | EUR/day | EUR/day | EUR/day | EUR/day | hours/yr | hours/yr | MWh_th/yr | MWh_th/yr | MWh_th/yr | MWh_el/yr | MWh_input/year | EUR/yr | EUR/yr | EUR/yr | EUR/yr | EUR/yr | EUR/yr | EUR/yr | EUR/yr | EUR/yr | EUR/yr |  | Heat pump | EUR | 4500000 | Regular annual expenses (heat pump specific) | EUR/yr | 66000 | Investment costs: equipment, installation, heat exchangers | EUR | 500000 | 0% | Regular annual expenses | EUR/yr | 50000 | 0% | Investment costs: equipment, installation, heat exchangers | EUR | 500000 | Regular annual expenses | EUR/yr | 50000
|  | Labels each characteristic day (e.g. Winter day, Summer weekend) | Number of days that each typical day represents across the entire year | Total thermal energy (waste heat) available from the data centre on that typical day | Amount of the available waste heat that is actually used in the system (e.g. heat pump) | Number of hours the system is running | Number of full-load-hour equivalents (MWh_th provided by heat pump / heat pump capacity) | Total heat delivered to the district heating grid, coming from both the heat pump and booster | Amount of electricity consumed by the heat pump to extract and upgrade the waste heat | If additional heating is needed, this reflects the fuel consumption of a booster heater | Daily cost for the waste heat based on a variable (usage-based) contract with a negotiated price. These Waste heat costs are part of SRMC. | Total electricity cost for operating the heat pump on that day | Electricity costs associated with additional or auxiliary components of the system (not the HP) (so SRMC) | Cost of fuel used by the booster to supplement heating if necessary | Operating and maintenance costs that vary with usage, associated with the heat pump. | Operating and maintenance costs that vary with usage, associated with the booster unit. | Sum of all daily variable costs (electricity, fuel, O&M), excluding any subsidies. | Costs saved by not using an alternative (usually more expensive) heat production method. Considered as earnings. | Daily subsidies received for using waste heat from the data centre. Considered as earnings. | Daily cost under a fixed contract where the buyer pays for a set amount of heat, used or not. These Waste heat costs are NOT part of SRMC. | Number of hours the system is running | Number of full-load-hour equivalents (MWh_th provided by heat pump / heat pump capacity) | Total thermal energy that the data centre can provide over the year | Amount of waste heat actually utilized by the heat recovery system (e.g., heat pump) over the year | Final thermal output per year fed into the district heating grid after processing via heat pumps and/or booster | Total electricity consumed annually by the heat pump to upgrade low-temperature waste heat | Total input energy (electricity or fuel) consumed by the booster unit to meet temperature requirements or supplement the heat pump. | Annual cost for purchasing waste heat under a Pay-as-you-go model, where costs are based on actual heat usage. These costs are included in short-run marginal costs (SRMC). | Total annual electricity cost for operating the heat pump, based on hourly/daily rates and consumption. | Electricity costs for system components other than the heat pump (e.g., circulation pumps, control units). | Total cost of fuel or energy used by the booster unit across the year. These are the variable costs of the defined typical day | Annual operation and maintenance costs for the heat pump that depend on how much the system is used. | Annual operation and maintenance costs for the booster system | Sum of all variable operational costs excluding any subsidies or earnings from incentives. | Represents the annual savings by replacing traditional heat production (e.g., gas boilers) with recovered waste heat. | Financial incentives or payments received for recovering and using waste heat from the data centre. | Annual fixed costs for waste heat under a Take-or-pay contract, where payment is required regardless of actual usage. These are not part of SRMC. |  | Other heat pump related one time expenses | EUR | 0 | Regular annual expenses (booster specific) | EUR/yr | 2000 | Heat network | EUR | 126000 | 0% | Cost for waste heat p_0 (Take-or-pay contract) | EUR/yr | 0 | 0% | Heat network | EUR | 126000 | Cost for waste heat p_0 (Take-or-pay contract) | EUR/yr | 0
| 1 | Winter day | 94.6086 | 48 | 48 | 24 | 22.7874 | 68.1753 | 20.3622 | 0.50683 | 0 | 1722.2343 | 185.9327 | 38.8386 | 0 | 0 | 1947.0056 | 4431.3962 | 0 | 96 | 2270.6065 | 2155.8842 | 4541.2131 | 4541.2131 | 6449.9725 | 1926.4395 | 47.9508 | 0 | 162938.1867 | 17590.8342 | 3674.4668 | 0 | 0 | 184203.4877 | 419248.2146 | 0 | 9082.4261 |  | Booster | EUR | 75000 | Personnel | EUR/yr | 20000 | Planning | EUR | 50080 | 0% | Total annual operation independent expenses | EUR/yr | 50000 |  | Planning | EUR | 50080 | Total annual operation independent expenses | EUR/yr | 50000
| 2 | Spring / fall weekday | 126.7755 | 48 | 48 | 24 | 22.8515 | 67.8689 | 20.5545 | 0 | 0 | 1927.4058 | 97.3474 | 0 | 0 | 0 | 2024.7531 | 4072.1369 | 0 | 96 | 3042.6128 | 2897.0108 | 6085.2255 | 6085.2255 | 8604.122 | 2605.8068 | 0 | 0 | 244347.8881 | 12341.2659 | 0 | 0 | 0 | 256689.154 | 516247.3201 | 0 | 12170.451 |  | Grid costs | Grid costs and HEx 2 | 1550000 | Rent | EUR/yr | 0 | Total | EUR | 676080 | [5 empty] | Total | EUR | 676080
| 3 | Spring / fall weekend | 50.7102 | 48 | 48 | 24 | 22.8515 | 67.8689 | 20.5545 | 0 | 0 | 1381.3092 | 97.3474 | 0 | 0 | 0 | 1478.6566 | 4072.1369 | 0 | 96 | 1217.0451 | 1158.8043 | 2434.0902 | 2434.0902 | 3441.6488 | 1042.3227 | 0 | 0 | 70046.4849 | 4936.5064 | 0 | 0 | 0 | 74982.9912 | 206498.928 | 0 | 4868.1804 |  | Planning | EUR | 490000 | Cost for waste heat (Take-or-pay contract) | EUR/yr | 34767.5272
| 4 | Summer weekday | 64.3339 | 48 | 36.4133 | 23 | 16.2635 | 48.3025 | 12.3771 | 0 | 0 | 1143.086 | 58.5484 | 0 | 0 | 0 | 1201.6344 | 1932.0986 | 0 | 96 | 1479.6786 | 1046.2908 | 3088.0249 | 2342.6084 | 3107.4836 | 796.2639 | 0 | 0 | 73539.1256 | 3766.6468 | 0 | 0 | 0 | 77305.7724 | 124299.3429 | 0 | 6176.0498 |  | Total | EUR | 6615000 | Heat pump: Electricity - grid fee and other electrical capacity-related costs | EUR/yr | 150000
| 5 | Summer weekend | 25.7335 | 48 | 37.9965 | 24 | 16.9706 | 50.4026 | 12.9152 | 0 | 0 | 788.4402 | 61.094 | 0 | 0 | 0 | 849.5342 | 2772.1414 | 0 | 96 | 617.605 | 436.7127 | 1235.21 | 977.7844 | 1297.0366 | 332.3536 | 0 | 0 | 20289.3581 | 1572.1656 | 0 | 0 | 0 | 21861.5237 | 71337.0142 | 0 | 2470.4199 |  | CAPEX Investment subsidies |  |  | Booster: Electricity/Fuel - grid fee and other capacity-related costs | EUR/yr | 75757.5758 | CAPEX Investment subsidies |  |  | Share received by Contractor 1 | Annual variable costs |  |  | Share paid by Contractor 1 | CAPEX Investment subsidies |  |  | Annual variable costs
| 6 | Maintenance of HP | 2.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Heat pump | EUR | 1800000 | Total annual operation independent expenses | EUR/yr | 348525.103 | Total subsidies | EUR | 0 | 0% | Variable O&M costs per year | EUR/yr | 32761.8431 | 0% | Total subsidies | EUR | 0 | Variable O&M costs per yr | EUR/yr | 32761.8431
| 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Booster | EUR | 0 | Annual operation independent O&M expenses: heat recovery share paid by Contractor 1 |  |  | Total | EUR | 0 |  | Total annual operation dependent expenses | EUR/yr | 32761.8431 |  | Total | EUR | 0 | Total annual operation dependent expenses | EUR/yr | 32761.8431
| 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total | EUR | 1800000 | Regular annual expenses | EUR/yr | 0
| 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAPEX decommissioning |  |  | Cost for waste heat p_0 (Take-or-pay contract) | EUR/yr | 0
| 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Decommission costs in current EUR | EUR | 0 | Total | EUR | 0
| 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Residual value in current EUR | EUR | 0
| 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total | EUR | 0 | Annual variable costs
| 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAPEX heat recovery share paid by Contractor 1 |  |  | Waste heat costs per year (Pay-as-you-go contract) | EUR/yr | 0
| 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total investment paid by Contractor 1 | EUR | 0 | Electricity cost HP per year | EUR/yr | 571161.0435 | [8 empty] | Total net investment needs | EUR | 676080 | Total annual costs | EUR/yr | 82761.8431
| 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Subsidies received for heat reciovery received by Contractor 1 | EUR | 0 | Electricity costs auxiliary energy | EUR/yr | 40207.4188 | [8 empty] | Capital recovery factor | 1/year | 9.634%
| 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total | EUR | 0 | Fuel costs Booster per year | EUR/yr | 3674.4668 | [8 empty] | Annualized investment | EUR/yr | 65135.0938 | Annual earnings
| 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Variable O&M costs HP per year | EUR/yr | 0 | [11 empty] | Earnings (waste heat paid by Contractor 1) | EUR/yr | 34767.5272
| 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total net investment needs | EUR | 4815000 | Variable O&M costs Booster per year | EUR/yr | 0 | [11 empty] | Total Annual earnings | EUR/yr | 34767.5272
| 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Capital recovery factor | 1/year | 9.634% | Total annual operation dependent expenses | EUR/yr | 615042.9291
| 20 | 20 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Annualized investment | EUR/yr | 463888.1148 | Annual variable costs: heat recovery share paid for by Contractor 1 | [10 empty] | Annual remaining electricity costs for active cooling |  |  | Annual avoided electricity costs for active cooling
|  |  | 365 | [17 empty] | 8627.548 | 7694.7027 | 17383.7636 | 16380.9215 | 22900.2635 | 6703.1865 | 47.9508 | 0 | 571161.0435 | 40207.4188 | 3674.4668 | 0 | 0 | 615042.9291 | 1337630.8197 | 0 | 34767.5272 |  |  |  |  | Variable O&M costs per year | EUR/yr | 0 | [8 empty] | Remaining electricity costs for cooling | EUR/yr | 13012.4946 | Avoided electricity costs for cooling | EUR/yr | 121445.7164
[31 empty] | Average variable costs per MWh and typical year |  | EUR/MWh_provided_to_grid | 26.8575 | 58.4112 | 0 | 1.5182 | EUR/MWh provided to grid |  |  |  | Total | EUR | 0 | [8 empty] | Total Annual avoided costs | EUR/yr | 13012.4946 | Total Annual avoided costs | EUR/yr | 121445.7164
Technical, energy-related and economic parameters Contractor 2 / Data centre Operator
| Typical Days | Name of Typical Day | Days of Typical Day in Typical Year | Available heat from DC per day | Used heat from DC per day | Avoided electricity demand for active cooling | Remaining electricity demand for active cooling |  |  |  |  | Avoided electricity costs due to reduced active cooling | Remaining electricity costs for active cooling | Energy costs under price p_0 per day paid to external entity | Variable O&M costs per day | Waste heat earnings per day in case of Pay-as-you-go based on negotiated price p_1 between Contractor 1 and Contractor 2 | Waste heat earnings if Take-or-pay contract based on negotiated price p_1 between Contractor 1 and Contractor 2 | [5 empty] | Available heat from DC per year | Used heat from DC per year | Avoided electricity costs due to reduced active cooling | Remaining electricity costs for active cooling | Energy costs under price p_0 per year paid to external entity | Variable O&M costs per year | Avoided electricity demand for active cooling | Remaining electricity demand for active cooling | Waste heat earnings per day in case of Pay-as-you-go based on negotiated price p_1 between Contractor 1 and Contractor 2 per year | Waste heat earnings if Take-or-pay contract based on negotiated price p_1 between Contractor 1 and Contractor 2 per year |  | Costs per year |  | Earnings for utilized waste heat provided by DC per year | Earnings due to avoided electricity costs for active cooling
| - |  | days | MWh_th/day | MWh_th/day | MWh_el/day | MWh_el/day |  |  |  |  | EUR/day | EUR/day | EUR/day | EUR / day | EUR / day | EUR/day | [5 empty] | MWh_th/year | MWh_th/year | EUR/yr | EUR/yr | EUR/yr | EUR/yr | MWh_el/yr | MWh_el/year | EUR/yr | EUR/yr |  | EUR/yr |  | EUR/yr | EUR/yr | [18 empty] | Total earnings | EUR/yr | 34767.5272
|  | Labels each characteristic day (e.g. Winter day, Summer weekend) | Number of days that each typical day represents across the entire year | Total thermal energy (waste heat) available from the data centre on that typical day | Amount of the available waste heat that is actually used in the system (e.g. heat pump) | Total AVOIDED electricity due to less active cooling needs. (THIS ARE SAVINGS) | Total remaining electricity demand for active cooling |  |  |  |  | Total hourly REDUCED electricity costs due to less active cooling needs. (THIS ARE SAVINGS) | Total hourly remaining electricity costs for active cooling | Waste heat cost based on price p_0 that is paid at the border between data centre cooling and waste heat recovery system under Take-or-Pay conditions | These are the operation and maintenance costs that vary depending on how much of the heat recovery system is used | Revenue generated for the data centre based on actual usage and negotiated price. These waste heat costs are part of SRMC. | Guaranteed revenue for the data centre based on fixed contractual payments.
| 1 | Winter day | 94.6086 | 48 | 48 | 1.52 | 0 |  |  |  |  | 126.7507 | 0 | 0 | 96 | 0 | 96 | [5 empty] | 4541.2131 | 4541.2131 | 11991.7038 | 0 | 0 | 9082.4261 | 143.8051 | 0 | 0 | 9082.4261 |  | 9082.4261 |  | 9082.4261 | 11991.7038
| 2 | Spring / fall weekday | 126.7755 | 48 | 48 | 4.8933 | -4.1448e-17 |  |  |  |  | 452.8068 | -4.9199e-15 | 0 | 96 | 0 | 96 | [5 empty] | 6085.2255 | 6085.2255 | 57404.8227 | -6.2373e-13 | 0 | 12170.451 | 620.3549 | -5.2546e-15 | 0 | 12170.451 |  | 12170.451 |  | 12170.451 | 57404.8227 |  |  |  |  | Annual costs for heat recovery paid by Contractor 1 | EUR/yr | 0
| 3 | Spring / fall weekend | 50.7102 | 48 | 48 | 4.8933 | -4.1448e-17 |  |  |  |  | 309.3287 | -2.9379e-15 | 0 | 96 | 0 | 96 | [5 empty] | 2434.0902 | 2434.0902 | 15686.1224 | -1.4898e-13 | 0 | 4868.1804 | 248.142 | -2.1019e-15 | 0 | 4868.1804 |  | 4868.1804 |  | 4868.1804 | 15686.1224 |  | Underlying assumptions on Waste heat-contract (used to determine SRMC) |  |  | Total annual costs, incl. Heat recovery costs paid by Contractor 1 | EUR/yr | 963568.0321
| 4 | Summer weekday | 64.3339 | 48 | 36.4133 | 4.8551 | 1.5449 |  |  |  |  | 443.5394 | 170.2286 | 0 | 72.8266 | 0 | 96 | [5 empty] | 3088.0249 | 2342.6084 | 28534.5999 | 10951.4596 | 0 | 4685.2168 | 312.3478 | 99.3889 | 0 | 6176.0498 |  | 4685.2168 |  | 6176.0498 | 28534.5999 |  | Share Take-or-pay Contract |  | 100%
| 5 | Summer weekend | 25.7335 | 48 | 37.9965 | 5.0662 | 1.3338 |  |  |  |  | 304.2126 | 80.0914 | 0 | 75.993 | 0 | 96 | [5 empty] | 1235.21 | 977.7844 | 7828.4676 | 2061.035 | 0 | 1955.5687 | 130.3712 | 34.3234 | 0 | 2470.4199 |  | 1955.5687 |  | 2470.4199 | 7828.4676 |  | Share Pay-as-you-go Contract |  | 0% | Annual subsidies (earnings)
| 6 | Maintenance of HP | 2.8383 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | Average waste heat price per heat feed into grid | EUR/MWh_provided to grid | 1.5182 | Annual operation independent subsidies for heat pump (average for project lifetime) | EUR/yr | 0
| 7 | 7 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | Average waste heat price per waste heat utilized in Heat Pump | EUR/MWh_waste_heat_utilized | 2.1224 | Annual subsidies for utilized waste heat (average for project lifetime) | EUR/yr | 0
| 8 | 8 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | Average waste heat price per heat provided by DC | EUR/MWh_waste_heat_provided_by_DC | 2 | Total Annual subsidies | EUR/yr | 0
| 9 | 9 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  |  | Avoided variable costs (SRMC) of alternative production (earnings)
| 10 | 10 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  |  | Total avoided SRMC | EUR/yr | 1337630.8197
| 11 | 11 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 12 | 12 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  |  | Total earnings | EUR/yr | 1337630.8197
| 13 | 13 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 14 | 14 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 15 | 15 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 16 | 16 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  |  | Total annual expenses | EUR/yr | 1427456.1469
| 17 | 17 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  |  | Total annual heat provided | MWh/year | 22900.2635
| 18 | 18 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  |  |  |  | Total costs of heat (LRMC) | EUR/MWh | 62.3336
| 19 | 19 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
| 20 | 20 | 0 | 0.024 | 0 | 0 | 0.0032 |  |  |  |  | 0 | 0.32 | 0 | 0 | 0 | 0.048 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
|  |  | 365 | [19 empty] | 17383.7636 | 16380.9215 | 121445.7164 | 13012.4946 | 0 | 32761.8431 | 1455.021 | 133.7123 | 0 | 34767.5272 |  | 32761.8431 |  | 34767.5272 | 121445.7164 |  | Go to Main Results
[31 empty] | Average variable costs per MWh and typical year |  | EUR/MWh_used_from_DC | 2 | EUR/MWh_used_from_DC | 2.1224 | 7.4139
Technical, Energy-related and Economic parameters Contractor 1 / District heating Operator
| Typical days | Name of typical day | Days of Typical Day in Typical Year | Average Flow Temperature of data centre cooling system | Average flow temperature HP, source in | Average DH supply line temperature | Average Required Temperature Sink Out | Average DH return line temperature | Average Temperature Heat Pump Sink In
| - |  | days | °C | °C | °C | °C | °C | °C
|  | Labels each characteristic day (e.g. Winter day, Summer weekend) | Number of days that each typical day represents across the entire year | Flow Temperature of the cooling system of the DC | Flow Temperature HP equals the temperature of the cooling system reduced by delta T of the heat exchanger | The required supply temperature for the district heating grid. | Temperature required by the DH grid and needs to be provided by HP + booster (may be higher than what HP alone can deliver). | The return temperature of the district heating network. | Inlet temperature into the heat pump from the sink (DH side).
| 1 | Winter day | 94.6086 | 40 | 37 | 82.4306 | 85.4306 | 45 | 48
| 2 | Spring / fall weekday | 126.7755 | 40 | 37 | 83.125 | 86.125 | 45 | 48
| 3 | Spring / fall weekend | 50.7102 | 40 | 37 | 83.125 | 86.125 | 45 | 48
| 4 | Summer weekday | 64.3339 | 40 | 37 | 60 | 63 | 45 | 48
| 5 | Summer weekend | 25.7335 | 40 | 37 | 60 | 63 | 45 | 48
| 6 | Maintenance of HP | 2.8383 | 40 | 37 | 71.5625 | 74.5625 | 45 | 48
| 7 | 7 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 8 | 8 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 9 | 9 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 10 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 11 | 11 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 12 | 12 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 13 | 13 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 14 | 14 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 15 | 15 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 16 | 16 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 17 | 17 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 18 | 18 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 19 | 19 | 0 | 0 | 0 | 0 | 3 | 0 | 3
| 20 | 20 | 0 | 30 | 27 | 83.3056 | 86.3056 | 43.125 | 46.125
365
|  |  | Annual averages | 40 | 37 | 77.1488 | 80.1488 | 45 | 48

## Calculation IRR
Go to Content Sheet
Header
Item / unit
User input
Cell with formula
Go to content
Input - not used for calculation
Control cells
Check settings / input data, there might be some error
| Contractor 1 / DH Operator |  |  | Time period | t0 | t1 | t2 | t3 | t4 | t5 | t6 | t7 | t8 | t9 | t10 | t11 | t12 | t13 | t14 | t15 | t16 | t17 | t18 | t19 | t20 | t21 | t22 | t23 | t24 | t25
| Depreciation time of project / Calculatory lifetime | 15 | years | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| CAPEX (total, incl. Lump-sum subsidies) | 4815000 | EUR |  | t0: -4815000
| OPEX - Fixed costs (Total) incl. Waste heat payment to Contractor 2 / DC Operator (Take-or-Pay) | 348525.103 | EUR/yr |  |  | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | -348525.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OPEX - Variable costs (Total) incl. Waste heat payment to Contractor 2 / DC Operator (Pay-as-you-go) | 615042.9291 | EUR/yr |  |  | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | -615042.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Sum |  |  |  | -4815000 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | -963568.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Earnings - Avoided variable costs (SRMC) of alternative production (i.e. refrence marginal heat costs) | 1337630.8197 | EUR/yr |  |  | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 1337630.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net earnings |  |  |  | -4815000 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 374062.7877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Internal Rate of Return |  | 1.98 % |  | t0: 1.976%
| Expected IRR as defined in Project Sheet |  | 5% |  | t0: Internal Rate of Return lower than expected IRR: IRR/expected IRR =0.396
| Contractor 2 / DC Operator |  |  | Time period | t0 | t1 | t2 | t3 | t4 | t5 | t6 | t7 | t8 | t9 | t10 | t11 | t12 | t13 | t14 | t15 | t16 | t17 | t18 | t19 | t20 | t21 | t22 | t23 | t24 | t25
| Depreciation time of project / Calculatory lifetime | 15 | years | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| CAPEX (total, incl. lump-sum subsidies) | 676080 | EUR |  | Internal Rate of Return lower than expected IRR: IRR/expected IRR =0.396 t0: -676080
| OPEX - fixed costs (total) | 50000 | EUR/yr |  |  | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | -50000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OPEX - variable costs (total) | 32761.8431 | EUR/yr |  |  | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | -32761.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Sum |  |  |  | -676080 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | -82761.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Earnings - Payments from Contractor 1 / DH Operator | 34767.5272 | EUR/yr |  |  | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 34767.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reduced electricity costs for active cooling | 121445.7164 | EUR/yr |  |  | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 121445.7164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net earnings |  |  |  | -676080 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 73451.4006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Internal Rate of Return |  | 6.83 %

## Additional Information
Go to Content
Abbreviations:
HP … heat pump
DH … district heating
DC … data centre
WH … waste heat
Description on how to add additional links is given in the VBA-Macro. Basically add a Excel to the Source cell (e.g. ='Project Setting'!D20) in Column B in this sheet. Only the xlsb version of the tool contains the Macro.
| Variable / Link to return | Variable (German) - bislang automatisierte Übersetzung | Description | Beschreibung -- automatisierte Übersetzung
Project Sheet | Generating capacity | Erzeugungskapazität
| Technical lifetime | Technische Lebensdauer
| COP - nominal | COP – Nennwert
| Capacity of waste heat stream (MW) at nominal operation conditions | Kapazität des Abwärmestroms (MWh) bei Nennbetriebsbedingungen
| Nominal temperature - heat pump source in | Nenntemperatur – Wärmepumpe Quelle Ein
| Nominal temperature - heat pump source out | Nenntemperatur – Wärmepumpe Quelle Aus
| Nominal temperature - heat pump sink out | Nenntemperatur – Wärmepumpen-Senke Ausgang
| HEx 2: Heat exchanger (HP - district heating network) delta T | HEx 2: Wärmetauscher (HP – Fernwärmenetz) Delta T
| HEx 1: Heat exchanger (HP - data centre cooling system) delta T | HEx 1: Wärmetauscher (HP – Rechenzentrumskühlsystem) Delta T
| Nominal Temperature - Heat Pump Sink In | Nenntemperatur – Wärmepumpen-Senke Eingang
| Upper temperature limit - Heat pump Sink Out | Obergrenze der Temperatur – Wärmepumpen-Senke Ausgang
| Exponent for capacity drop if temperature spread of sink decreases | Exponent für Kapazitätsabfall bei sinkender Temperaturdifferenz der Senke | Defines, the upper flow rate capacity compared to the nominal flow rate at nominal temperature difference at the heat sink and nominal capacity of heat pump. If the temperature difference drops, then in order to transfer the same amount of heat, the flow rate must be increased instead. This parameter allows to specifiy the upper limit of the increase flow rate capacity. If this limit is reached, then the heat pump power output must be reduced. Please be aware that this is an aproximation. First, it is not unplausible, that the piping system supports higher low rates than those of nominal capacity and thus a lower temperature difference does not neccessarily lead to decrease capacity. Alternatively, the heat pump could deliver higher-than-neccessary Heat Pump Sink Out Temperature (at the expense of a lower COP) and thus circumvent the flow rate restriction. We propose a default close to Zero. The actual used formula is as follows: Nominal_Capacity * MIN(1, (MAX(1, Temperature_Spread_between_DH_supply_and_return_line)/HP_Temperature_spread_at_nominal_operature)^DEFINED_EXPONENT ) | Definiert die obere Durchflusskapazität im Vergleich zum Nenn-Durchfluss bei Nenn-Temperaturdifferenz am Wärmesenke und Nennleistung der Wärmepumpe. Wenn die Temperaturdifferenz sinkt, muss stattdessen der Durchfluss erhöht werden, um die gleiche Wärmemenge zu übertragen. Mit diesem Parameter kann die Obergrenze der erhöhten Durchflusskapazität festgelegt werden. Wenn diese Grenze erreicht ist, muss die Leistung der Wärmepumpe reduziert werden. Bitte beachten Sie, dass es sich hierbei um eine Annäherung handelt. Erstens ist es nicht unwahrscheinlich, dass das Rohrleitungssystem höhere Durchflussraten als die Nennleistung unterstützt und somit eine geringere Temperaturdifferenz nicht unbedingt zu einer Verringerung der Leistung führt. Alternativ könnte die Wärmepumpe eine höhere als die erforderliche Wärmepumpen-Sink-Out-Temperatur liefern (auf Kosten eines niedrigeren COP) und so die Durchflussbeschränkung umgehen. Wir schlagen einen Standardwert nahe Null vor. Die tatsächlich verwendete Formel lautet wie folgt: Nennleistung * MIN(1, (MAX(1,Temperaturunterschied zwischen Vor- und Rücklaufleitung)/HP_Temperaturunterschied bei Nennbetriebstemperatur)^DEFINED_EXPONENT )
| S - Source | S – Quelle | Empirical default value for impact of increased source temperature on the COP of the heat pump. Please check thoroughly if the default value is applicable for the intended heat pump. The actual used formula is as follows: =ABS(DEFINED_S_SOURCE_VALUE) * (Actual_T_source_HP_in - Nominal_T_source_HP_in) | Empirischer Standardwert für den Einfluss einer erhöhten Quellentemperatur auf den COP der Wärmepumpe. Bitte überprüfen Sie sorgfältig, ob der Standardwert für die vorgesehene Wärmepumpe geeignet ist. Die tatsächlich verwendete Formel lautet wie folgt: =ABS(DEFINED_S_SOURCE_VALUE) * (Actual_T_source_HP_in - Nominal_T_source_HP_in)
| S - Flow | S – Vorlauf | Empirical default value for impact of increasing sink_out temperature (Supply line temperature of District heating network) on the COP of the heat pump. Please check thoroughly if the default value is applicable for the intended heat pump. The actual used formula is as follows: =ABS(DEFINED_S_FLOW_VALUE) * (Nominal_T_sink_HP_out - Actual_T_sink_HP_out) | Empirischer Standardwert für den Einfluss einer erhöhten Sink_Out-Temperatur (Vorlauftemperatur des Fernwärmenetzes) auf den COP der Wärmepumpe. Bitte überprüfen Sie sorgfältig, ob der Standardwert für die vorgesehene Wärmepumpe geeignet ist. Die tatsächlich verwendete Formel lautet wie folgt: =ABS(DEFINED_S_FLOW_VALUE) * (Nominal_T_sink_HP_out - Actual_T_sink_HP_out)
| S - Return | S – Rücklauf | Empirical default value (DIRECT PROPORTIONAL) for the impact of increasing heat sink_in temperature (Return line temperature of district heating network) on the COP of the heat pump. Please check thoroughly if the default value is applicable for the intended heat pump. The impact of the increasing / decreasing return line temperature of DH is not clear at this stage (to the authors of this tool). Thus we suggest to use a value of Zero (no impact) unless more information is available. The actual used formula is as follows: =DEFINED_S_RETURN_VALUE * (Actual_T_sink_HP_out - Nominal_T_sink_HP_out) If a value > 0 (POSITIVE NUMBER) is defined, then the EFFICIENCY of the heat pump INCREASES WITH INCREASING inlet TEMPERATURE on the heat sink side (Return line temperature). If a value < 0 (negative number) is defined, then the efficiency of the heat pump decreases with increasing inlet temperature on the heat sink side (Return line temperature). | Empirischer Standardwert (DIREKT PROPORTIONAL) für den Einfluss einer steigenden Kühlkörpertemperatur (Rücklauftemperatur des Fernwärmenetzes) auf den COP der Wärmepumpe. Bitte überprüfen Sie sorgfältig, ob der Standardwert für die vorgesehene Wärmepumpe geeignet ist. Der Einfluss der steigenden/fallenden Rücklauftemperatur der Fernwärme ist zum jetzigen Zeitpunkt (den Autoren dieses Tools) nicht klar. Daher empfehlen wir, den Wert Null (kein Einfluss) zu verwenden, sofern keine weiteren Informationen verfügbar sind. Die tatsächlich verwendete Formel lautet wie folgt: =DEFINED_S_RETURN_VALUE * (Actual_T_sink_HP_out - Nominal_T_sink_HP_out) Wenn ein Wert > 0 (POSITIVE ZAHL) definiert ist, steigt die EFFIZIENZ der Wärmepumpe mit steigender Einlasstemperatur auf der Kühlkörperseite (Rücklauftemperatur). Wenn ein Wert < 0 (negative Zahl) definiert ist, sinkt die Effizienz der Wärmepumpe mit steigender Einlasstemperatur auf der Kühlkörperseite (Rücklauftemperatur).
| Share of heat loss in heat exchangers & pipes from HP output | Anteil des Wärmeverlusts in Wärmetauschern und Rohrleitungen aus der Wärmepumpenleistung | Energy losses that occur between the heat pump and the district heating grid. Consider all losses caused by additional piping, heat exchanger HEx 2, etc. | Energieverluste, die zwischen der Wärmepumpe und dem Fernwärmenetz auftreten. Berücksichtigen Sie alle Verluste, die durch zusätzliche Rohrleitungen, den Wärmetauscher HEx 2 usw. verursacht werden.
| Specific investment costs (equipment, installation) | Spezifische Investitionskosten (Ausrüstung, Installation)
| Investment costs | Investitionskosten
| Other one-time expenses | Sonstige einmalige Ausgaben
| Total one-time expenses and costs excl. planning costs | Gesamtbetrag der einmaligen Ausgaben und Kosten ohne Planungskosten
| Regular annual expenses (heat pump specific) | Regelmäßige jährliche Ausgaben (wärmepumpenspezifisch)
| O&M Costs - fix | Betriebs- und Wartungskosten – fest
| Total operation independent O&M costs related to heat pump: regular annual expenses (heat pump specific) + O&M Costs - fix * nominal capacity of heat pump | Gesamtbetriebskosten unabhängig von Betrieb und Wartung im Zusammenhang mit der Wärmepumpe: Regelmäßige jährliche Ausgaben (wärmepumpenspezifisch) + Betriebskosten – Fix * Nennleistung der Wärmepumpe
| O&M Costs - variable (excl. electricity) | Betriebskosten – Variabel (ohne Strom)
| Electricity - grid fee and other electrical capacity-related costs | Jährliche leistungsbezogenen, verbrauchsunabhängigen Netzkosten und sonst. Strombereitstellungskosten (die nicht im Strompreis in Sheet >Definition of Typical Day> integriert sind) | Please make sure, that this cost components are not double counted, i.e. they are considered in >Project Setting< as well as in the electricity/fuel price in sheet >Definition of Typical Day< | Bitte stellen Sie sicher, dass diese Kostenkomponenten nicht doppelt berücksichtigt werden, d. h. dass sie sowohl in den >Project Setting< als auch im Strom-/Brennstoffpreis im Blatt >Definition of Typical Day< berücksichtigt werden.
| Electricity - grid fee and other electricity consumption-related costs | Verbrauchsunabhängigen Netz- und sonst. Strom-/Brennstoffbereitstellungskosten (die nicht im Strompreis in Sheet >Definition of Typical Day> integriert sind) | Please make sure, that this cost components are not double counted, i.e. they are considered in >Project Setting< as well as in the electricity/fuel price in sheet >Definition of Typical Day< | Bitte stellen Sie sicher, dass diese Kostenkomponenten nicht doppelt berücksichtigt werden, d. h. dass sie sowohl in den >Project Setting< als auch im Strom-/Brennstoffpreis im Blatt >Definition of Typical Day< berücksichtigt werden.
| S1 (one-time, lump sum per MW) | S1 (einmalig, Pauschalbetrag pro MW)
| S1 total lump sum subsidies | S1 Gesamtpauschalzuschüsse
| S2 (annually) for given number of yrs | S2 (jährlich) für eine bestimmte Anzahl von Jahren | S2 defines subsidies provided by the public per MW_th installed capacity, independant of acual operation. If the subsidies are not provided for the entire project period but for a shorter period, don't adjust the subsidy level, but the number of years, for which these subsidies are given. | S2 definiert die von der öffentlichen Hand gewährten Subventionen pro MW_th installierter Leistung, unabhängig vom tatsächlichen Betrieb. Wenn die Subventionen nicht für die gesamte Projektdauer, sondern für einen kürzeren Zeitraum gewährt werden, passen Sie nicht die Höhe der Subventionen an, sondern die Anzahl der Jahre, für die diese Subventionen gewährt werden.
| S2 given for number of years | S2 für eine bestimmte Anzahl von Jahren | Define here the number of years, for which the subsidies S2 are granted. | Legen Sie hier die Anzahl der Jahre fest, für die die Subventionen S2 gewährt werden.
| S2 (annually), average for calculatory project lifetime | S2 (jährlich, diskontiert), Durchschnitt für die rechnerische Projektlebensdauer
| S3 (annually, based on supplied waste heat (WH) by DC). PLEASE BE AWARE THAT THIS KIND OF SUBSIDY IS ONLY PROVIDED BY SOME COUNTRIES, E.G. GERMANY | S3 (jährlich, basierend auf der von DC gelieferten Abwärme (WH)) | S3 defines subsidies provided by the public per MWh_th waste heat utilized by the heat pump. In contrast to S2, these subsidies dependant on the acual operation. If the subsidies are not provided for the entire project period but for a shorter period, don't adjust the subsidy level, but the number of years, for which these subsidies are given. | S3 definiert Subventionen, die von der Öffentlichkeit pro MWh_th Abwärme, die von der Wärmepumpe genutzt wird, gewährt werden. Im Gegensatz zu S2 sind diese Subventionen vom tatsächlichen Betrieb abhängig. Wenn die Subventionen nicht für die gesamte Projektdauer, sondern für einen kürzeren Zeitraum gewährt werden, passen Sie nicht die Höhe der Subventionen an, sondern die Anzahl der Jahre, für die diese Subventionen gewährt werden.
| S3 given for number of years | S3 für eine bestimmte Anzahl von Jahren | Define here the number of years, for which the subsidies S3 are granted. | Geben Sie hier die Anzahl der Jahre an, für die die Subventionen S3 gewährt werden.
| S3, average for calculatory project lifetime | S3, Durchschnitt über die kalkulatorische Projektlaufzeit
| Consider subsidies (S3) in dispatch | S3 in der Einsatzentscheidung berücksichtigen
| Generating capacity | Erzeugungskapazität
| Efficiency | Effizienz
| Specific investment costs | Spezifische Investitionskosten
| Investment costs | Investitionskosten
| Other one-time expenses | Sonstige einmalige Ausgaben
| Total one-time expenses and costs excl. Planning costs | Gesamtbetrag der einmaligen Ausgaben und Kosten ohne Planungskosten
| Regular annual expenses (booster specific) | Regelmäßige jährliche Ausgaben (booster-spezifisch)
| O&M Costs - fix | Betriebs- und Wartungskosten – fest
| Total operation independent O&M costs related to booster | Gesamtbetriebskosten unabhängig vom Booster
| O&M Costs - Variable | Betriebs- und Wartungskosten – variabel
| Electricity / fuel - grid fee and other capacity-related costs | Jährliche leistungsbezogenen, verbrauchsunabhängigen Netzkosten und sonst. Strom-/Brennstoffbereitstellungskosten (die nicht im Strompreis in Sheet >Definition of Typical Day> integriert sind) | Please make sure, that this cost components are not double counted, i.e. they are considered in >Project Setting< as well as in the electricity/fuel price in sheet >Definition of Typical Day< | Bitte stellen Sie sicher, dass diese Kostenkomponenten nicht doppelt berücksichtigt werden, d. h. dass sie sowohl in den >Project Setting< als auch im Strom-/Brennstoffpreis im Blatt >Definition of Typical Day< berücksichtigt werden.
| Electricity / fuel - grid fee and other consumption-related costs | Verbrauchsunabhängigen Netz- und sonst. Strom-/Brennstoffbereitstellungskosten (die nicht im Strompreis in Sheet >Definition of Typical Day> integriert sind) | Please make sure, that this cost components are not double counted, i.e. they are considered in >Project Setting< as well as in the electricity/fuel price in sheet >Definition of Typical Day< | Bitte stellen Sie sicher, dass diese Kostenkomponenten nicht doppelt berücksichtigt werden, d. h. dass sie sowohl in den >Project Setting< als auch im Strom-/Brennstoffpreis im Blatt >Definition of Typical Day< berücksichtigt werden.
| S1 (one-time, lump sum per MW) | S1 (einmalig, Pauschale pro MW)
| Investment costs in HEx2 (equipment, installation, heat exchangers, one-time, lump-sum) | Investitionskosten (Ausrüstung, Installation, Wärmetauscher, einmalig, Pauschale)
| Investment costs for heat network from DH grid to B2 (see >Grid Costs<) | Investitionskosten für Wärmenetz (siehe >Netzkosten<)
| Planning costs [% total investment costs: Heat pump, booster, heat network, heat exchanger] | Planungskosten [% der Gesamtinvestitionskosten: Wärmepumpe, Booster, Wärmenetz]
| Total Investment costs (HP, booster, heat network, heat exchanger, etc.) | Gesamtinvestitionskosten (WP, Booster, Wärmenetz, Wärmetauscher usw.)
| Planning costs [absolute] | Planungskosten [absolut]
| Auxiliary electricity consumption (share of heat gen.) | Hilfsenergieverbrauch (Anteil an der Wärmeerzeugung)
| Personnel | Personal
| Rent | Miete
| Demolition costs | Abriss
| Residual value of investment at the end of the lifetime | Restwert der Investition am Ende der Lebensdauer
| Decommissioning after how many years | Stilllegung nach wie vielen Jahren
| Depreciation time of project / calculatory lifetime | Abschreibungsdauer des Projekts / kalkulatorische Lebensdauer
| Energy carrier price increase on top of inflation | Energiepreissteigerung zusätzlich zur Inflation
| Average interest rate of loans in real terms (excluding inflation) | Durchschnittlicher Realzinssatz für Darlehen (ohne Inflation)
| Expected interest rate on equity, again in real terms | Erwarteter Realzinssatz für Eigenkapital
| Share of equity capital on total financing | Anteil des Eigenkapitals an der Gesamtfinanzierung
| Corporate tax rate | Körperschaftssteuersatz
| Weighted average costs of capital (WACC) | Gewichtete durchschnittliche Kapitalkosten (WACC)
| Required (company internal) rate of return for such project | Erforderliche (unternehmensinterne) Rendite für ein solches Projekt
| Rate of return used in the subsequent calculations | In den nachfolgenden Berechnungen verwendete Rendite
| Capital recovery factor (annuity factor) | Kapitalrückflussfaktor (Annuitätenfaktor)
| Investment costs (equipment, installation, heat exchangers, one-time, lump sum) | Investitionskosten (Ausrüstung, Installation, Wärmetauscher, einmalig, Pauschalbetrag)
| Investment costs for heat network (see >Grid Costs<) | Investitionskosten für das Wärmenetz (siehe >Netzkosten<)
| Total one-time expenses and costs excl. Planning costs | Gesamtkosten einmalig ohne Planungskosten
| Planning costs [% Investment costs] | Planungskosten [% Investitionskosten]
| Planning costs [absolute] | Planungskosten [absolut]
| Regular annual expenses (WASTE HEAT RECOVERY specific) | Regelmäßige jährliche Kosten (spezifisch für ABWÄRMERÜCKGEWINNUNG)
| O&M Costs - Variable (incl. electricity) | Betriebs- und Wartungskosten – variabel (inkl. Strom)
| Heat price (Take-or-Pay) p_0 | Wärmepreis (Take-or-Pay) p_0
| S1 (one-time, lump sum) | S1 (einmalig, Pauschalbetrag)
| Depreciation time of project / Calculatory lifetime | Abschreibungsdauer des Projekts / Kalkulatorische Lebensdauer
| Average interest rate of loans in real terms (excluding inflation) | Durchschnittlicher Realzinssatz für Darlehen (ohne Inflation)
| Expected interest rate on equity, again in real terms | Erwarteter Realzinssatz für Eigenkapital
| Share of equity capital on total financing | Anteil des Eigenkapitals an der Gesamtfinanzierung
| Corporate tax rate | Körperschaftsteuersatz
| Weighted average costs of capital (WACC) | Gewichtete durchschnittliche Kapitalkosten (WACC)
| Required (company internal) rate of return for such project | Erforderliche (unternehmensinterne) Rendite für ein solches Projekt
| Rate of return used in the subsequent calculations | In den nachfolgenden Berechnungen verwendete Rendite
| Capital recovery factor (annuity factor) | Kapitalrückzahlungsfaktor (Annuitätenfaktor)
| Electricity - grid fee | Stromnetzentgelt (aktive Kühlung)
Grid Costs |  |  | This sheet is intended to support the calculation of the piping costs.
| Specific cost (including pipe works and joints) |  |  | Dieses Blatt dient zur Unterstützung der Berechnung der Rohrleitungskosten.
Definition of Typical Day | Name of typical day | Benennung der typischen Tage | The defined name used for displaying and some sort of documentation only and not directly used in any calculation. I.e, it does not trigger any kind of action within the calculations. | Die Bezeichnung dient ausschließlich der Anzeige und einer Art Dokumentation und wird nicht direkt in Berechnungen verwendet. Das heißt, es löst keinerlei Aktion innerhalb der Berechnungen aus.
| Season of typical day | Jahreszeit der typischen Tage | This is used for displaying and some sort of documentation only and not directly used in any calculation. I.e, it does not trigger any kind of action within the calculations. | Die Bezeichnung dient ausschließlich der Anzeige und einer Art Dokumentation und wird nicht direkt in Berechnungen verwendet. Das heißt, es löst keinerlei Aktion innerhalb der Berechnungen aus.
| Qualitative Description | Qualitative Beschreibung | This is used for displaying and some sort of documentation only and not directly used in any calculation. I.e, it does not trigger any kind of action within the calculations. | Dies dient ausschließlich der Anzeige und einer Art Dokumentation und wird nicht direkt in Berechnungen verwendet. Das heißt, es löst keinerlei Aktion innerhalb der Berechnungen aus.
| Electricity price auxiliary electricity (for simplicity, this price includes already grid fees, etc.). | Strompreis Hilfsstrom | Electricity price auxiliary electricity (for simplicity, this price includes already grid fees, etc.). The auxiliary electricity demand is defined as share (in %) on total heat generation in sheet >Project Settings< under "Other OPEX" | Strompreis für Hilfsenergie (der Einfachheit halber sind in diesem Preis bereits Netzentgelte usw. enthalten). Der Hilfsenergiebedarf wird als Anteil (in %) an der gesamten Wärmeerzeugung definiert und ist im Blatt >Project Settings< unter "Other OPEX"
| Available waste heat (DC heat source) | Verfügbare Abwärme (DC-Wärmequelle)
| Max heat demand - grid (HP heat sink) | Maximaler Wärmebedarf – Netz (WP-Wärmesenke)
| Heat source temperature (DC) / temperature of the cooling system before HEx 1 | Temperatur der Wärmequelle (DC) / Temperatur des Kühlsystems vor HEx 1 | Temperature (in °C) of the data centre's cooling water at the inlet of heat exchanger 1 (HEx 1) | Temperatur (in °C) des Kühlwassers des Rechenzentrums am Eintritt in Wärmetauscher 1 (HEx 1)
| DH supply line temperature* | Temperatur der Fernwärme-Vorlaufleitung | DH supply line temperature: Temperature at the DH feed-in point, equal to the heat pump sink out minus the temperature drop between the heat pump sink out temperature and the feed-in point district heating network (delta T heat exchanger). | Temperatur am Einspeisepunkt des Fernwärmenetzes, gleich der Auslasstemperatur der Wärmepumpe abzüglich des Temperaturabfalls zwischen der Auslasstemperatur der Wärmepumpe und dem Einspeisepunkt des Fernwärmenetzes (Delta T Wärmetauscher).
| DH return line temperature* | Temperatur der Fernwärme-Rücklaufleitung | DH return line temperature: Temperature heat pump sink in minus temperature drop (delta T heat exchanger) between temperature heat pump sink in and return point DH network | Einlasstemperatur der Wärmepumpe abzüglich des Temperaturabfalls (Delta T Wärmetauscher) zwischen der Einlasstemperatur der Wärmepumpe und dem Rücklaufpunkt des Fernwärmenetzes.
| Short-run marginal costs of alternative heat production | Kurzfristige Grenzkosten der alternativen Wärmeerzeugung
| Electricity price heat pump | Strompreis für die Wärmepumpe
| Energy price for energy used by booster | Energiepreis für den Energieverbrauch des Booster
| Data centre operator / waste heat provider: Electricity price for active cooling system | Rechenzentrumsbetreiber / Abwärmelieferant: Strompreis für das aktive Kühlsystem
| Data centre operator / waste heat provider: Share of active cooling (if heat is not taken up by Contractor 1) | Rechenzentrumsbetreiber / Abwärmelieferant: Anteil der aktiven Kühlung (falls die Wärme nicht von Auftragnehmer 1 entnommen wird)
Calculation Break-Even | The calculated break-even price for waste heat is the lower limit for the DC operator to receive to reach the break-even point under the predefined economic parameters. (Expected IRR and calculatory life time as defined in the Project Sheet) | Der berechnete Break-even-Preis für Abwärme stellt die Untergrenze dar, die der DC-Betreiber erhalten muss, um unter den vordefinierten wirtschaftlichen Parametern die Gewinnschwelle zu erreichen. (Erforderliche Kapitalrendite und kalkulatorische Nutzungsdauer gemäß Definition im Projektblatt)
| Contractor 2 / DC operator: Break-even waste heat price per MWh waste heat utilised in heat pump | Auftragnehmer 2 / DC-Betreiber: Break-even-Preis für Abwärme pro MWh in der Wärmepumpe genutzter Abwärme | If the Break-even waste heat price for Contractor 2 / DC Operator is below Zero, avoided costs (e.g. reduced electricity costs for cooling) outweight the projects costs, even if the waste heat is given for free. | Liegt der Break-even-Preis für Abwärme für Auftragnehmer 2 / DC-Betreiber unter Null, überwiegen die vermiedenen Kosten (z. B. geringere Stromkosten für die Kühlung) die Projektkosten, selbst wenn die Abwärme kostenlos zur Verfügung gestellt wird.
| LCOH - excl. payment to DC operator based on negotiated price p_1 between Contractor 1 and Contractor 2 | Durchschnittliche Wärmegestehungskosten (LCOH - Levelized costs of heat) – ohne Zahlung an den Rechenzentrumsbetreiber auf Basis des zwischen Auftragnehmer 1 und Auftragnehmer 2 ausgehandelten Preises p_1 | LCOH: Levelized costs of heat
| LCOH - incl. payment to DC operator based on negotiated price p_1 between Contractor 1 and Contractor 2 | Durchschnittliche Wärmegestehungskosten (LCOH - Levelized costs of heat) – einschließlich Zahlung an den Rechenzentrumsbetreiber auf Basis des zwischen Auftragnehmer 1 und Auftragnehmer 2 ausgehandelten Preises p_1 | LCOH: Levelized costs of heat
| LCOH - excl. payment to DC operator based on negotiated price p_1 between Contractor 1 and Contractor 2 excluding heat extraction system investment costs share paid by contractor 1 | Durchschnittliche Wärmegestehungskosten (LCOH - Levelized costs of heat) – ohne Zahlung an den Rechenzentrumsbetreiber auf Basis des zwischen Auftragnehmer 1 und Auftragnehmer 2 ausgehandelten Preises p_1, abzüglich des von Auftragnehmer 1 getragenen Anteils an den Investitionskosten für das Wärmeentnahmesystem | LCOH: Levelized costs of heat
| LCOH - incl. payment to DC operator based on negotiated price p_1 between Contractor 1 and Contractor 2 excluding heat extraction system investment costs share paid by contractor 1 | Durchschnittliche Wärmegestehungskosten (LCOH - Levelized costs of heat) – inkl. Zahlung an den Rechenzentrumsbetreiber auf Basis des zwischen Auftragnehmer 1 und Auftragnehmer 2 ausgehand | LCOH: Levelized costs of heat

## TechKatalogGWPA
Go to Content Sheet
| KWW-Technikkatalog Wärmeplanung 2024 | [10 empty] | Die angegebenen Parameter stellen bundesweite Durchschnittswerte dar. Tatsächliche Kosten können lokal z.T. erheblich abweichen und sollten daher im Einzelfall überprüft und ggf. den lokalen Umständen angepasst werden.
Der erste Technikkatalog Wärmeplanung wurde 2024 von einem Konsortium im Auftrag des Bundesministeriums für Wirtschaft und Klimaschutz (BMWK) sowie des Bundesministeriums für Wohnen, Stadtentwicklung und Bauwesen (BMWSB) erstellt. Der KWW-Technikkatalog baut auf dieser Arbeit auf.
| Technologie | Großwärmepumpe Abwärme (Kompressionswärmepumpe)
| Jahr | 2023
| technische Daten | Einheit |  |  |  |  | Unsicherheit ± | Referenzen | Anmerkungen |  | Kostenkurve | Spezifische Investitionskosten [€/kWth] = a*Leistung [MWth]^b
| thermische Leistung | MWth | 0.3 | 1.5 | 5 | 20 |  |  | H |  | Jahr | 2023 | 2030 | 2040
| Jahresarbeitszahl (JAZ), Durchschnitt/a |  | 4.2 | 4.2 | 4.2 | 4.2 | 10% | [5], [6] | A, B, C |  | Parameter a | 1274.4 | 1210.6 | 1146.9
| Lebensdauer | a | 25 | 25 | 25 | 25 |  | [1], [2] | G |  | Parameter b | -0.28 | -0.28 | -0.28
| Kosten (€2022, ohne MWSt.) | Einheit
| Spezifische Investitionskosten (inkl. Erschließungskosten) | €/kWth | 1861 | 1024 | 872 | 546 | 25% | [1]-[5] | A, D, E, J |  | Scope | Alle Kosten in €2023 und ohne MWSt.
| davon Anlagenkosten | % | 75 | 78 | 80 | 80 |  | [1]-[4]
| davon Installationskosten | % | 25 | 23 | 20 | 20 |  | [1]-[4] |  |  | Anmerkungen
| Investitionskosten gesamt | Tsd. € | 558 | 1536 | 4359 | 10923 | 25% | [1]-[5] | A, C, D |  | A | Basierend auf Kühlwasser, das von 25 auf 15 °C gekühlt wird. Die tatsächliche Entwicklung der Leistungszahloptimierung und reduzierten Investitionskosten hängt von der Entwicklung der Brennstoff- und Strompreise ab.
| jährliche Fixkosten O&M (ohne Energiekosten) | €/kWth*a | 47 | 26 | 22 | 14 |  | [3] | F |  | B | Typische JAZ von realisierten Anlagen. Die JAZ ist abhängig von der Vor-/Rücklauftemperatur des Wärmenetzes, vgl. z.B. [5].
[11 empty] | C | Basierend auf Projektbeispielen aus [6].
| Jahr | 2030 | [8 empty] | D | Preise beinhalten nur Wärmepumpe, Erschließungskosten werden hier nicht mit betrachtet. Es wird davon ausgegangen, dass Wärmepumpen wie Elektrokessel mit eingeschränktem Zugang angeschlossen sind. Kosten können höher liegen, wenn Installationen für den vollen Zugang bezahlen müssen [1].
| technische Daten | Einheit |  |  |  |  | Unsicherheit ± | Referenzen | Anmerkungen |  | E | Bei Wärmenetztemperaturen von 40-80 °C erhöht sich die spezifische Investition voraussichtlich um 15 %, da die Komponenten der Wärmepumpe für höhere Temperaturen (bzw. Druckstufen) ausgelegt werden müssen.
| thermische Leistung | MWth | 0.3 | 1.5 | 5 | 20 |  |  | H |  | F | Betrieb und Wartung beziehen sich auf die Wärmepumpe selbst einschließlich der Zusatzeinrichtungen, Gebäude usw. für die Wärmepumpe. Die Kosten beinhalten nicht Betriebs- und Wartungskosten für das Wärmenetz, Spitzenlast- oder Reserveeinheiten, Verwaltung bezüglich Endverbraucher usw.
| Jahresarbeitszahl (JAZ), Durchschnitt/a |  | 4.4 | 4.4 | 4.4 | 4.4 | 10% | [5], [6] | A, B, C |  | G | Die Lebensdauer kann zwischen 15 und 40 Jahren liegen (siehe [2])
| Lebensdauer | a | 28 | 28 | 28 | 28 |  | [1], [2] | G |  | H | Im TK von Baden-Württemberg wurden für Anlagen der Größe 1,5 MW und 5 MW Bandbreiten angegeben. Kosten- und technische Daten wurden für diese Stützanlagen hier linear interpoliert.
| Kosten (€2022, ohne MWSt.) | Einheit | [8 empty] | I | Es wird eine Kostenminderung um 10% bis 2040 (5% bis 2030) angenommen. In [1] wird keine Kostenminderung erwartet, in [3] eine höhere als hier (15% bis 2040).
| Spezifische Investitionskosten (inkl. Erschließungskosten) | €/kWth | 1768 | 973 | 828 | 519 | 35% | [1]-[5] | A, D, E, I, J |  | J | Streubreite der Erschließungskosten ist in der Praxis groß, da abhängig von Projekt, Quelle etc. Dies kann erhebliche Auswirkungen auf die Investitionskosten haben.
| davon Anlagenkosten | % | 75 | 78 | 80 | 80 |  | [1]-[4]
| davon Installationskosten | % | 25 | 23 | 20 | 20 |  | [1]-[4] |  |  | Referenzen
| Investitionskosten gesamt | Tsd. € | 530 | 1459 | 4141 | 10377 | 35% | [1]-[5] | A, C, D |  | [1] | KEA (2024): Technikkatalog Baden-Württemberg Version 1.1 (Stand Januar 2024)
| jährliche Fixkosten O&M (ohne Energiekosten) | €/kWth*a | 44 | 24 | 21 | 13 |  | [3] | F |  | [2] | DEA, Danish Energy Agency (2020): Technology Data for generation of electricity and district heating.
[11 empty] | [3] | AGFW-Praxisleitfaden Großwärmepumpen (2023).
[11 empty] | [4] | Pieper et.al., Allocation of investment costs for large-scale heat pumps supplying district heating, Energy Procedia 147 (2018) S. 358–367.
| Jahr | 2040 | [8 empty] | [5] | AGFW, Arbeitsgemeinschaft Fernwärme (2020): Perspektive der Fernwärme: Maßnahmenprogramm 2030.
| technische Daten | Einheit |  |  |  |  | Unsicherheit ± | Referenzen | Anmerkungen |  | [6] | Agora Energiewende, Fraunhofer IEG (2023): Roll-out von Großwärmepumpen in Deutschland. Strategien für den Markthochlauf in Wärmenetzen und Industrie.
| thermische Leistung | MWth | 0.3 | 1.5 | 5 | 20 |  |  | H
| Jahresarbeitszahl (JAZ), Durchschnitt/a |  | 4.6 | 4.6 | 4.6 | 4.6 | 10% | [5], [6] | A, B, C
| Lebensdauer | a | 25 | 25 | 25 | 25 |  | [1], [2] | G
| Kosten (€2022, ohne MWSt.) | Einheit
| Spezifische Investitionskosten (inkl. Erschließungskosten) | €/kWth | 1675 | 921 | 785 | 492 | 45% | [1]-[5] | A, D, E, I, J
| davon Anlagenkosten | % | 75 | 78 | 80 | 80 |  | [1]-[4]
| davon Installationskosten | % | 25 | 23 | 20 | 20 |  | [1]-[4]
| Investitionskosten gesamt | Tsd. € | 503 | 1382 | 3923 | 9831 | 45% | [1]-[5] | A, C, D
| jährliche Fixkosten O&M (ohne Energiekosten) | €/kWth*a | 42 | 23 | 20 | 12 |  | [3] | F
KWW-Technikkatalog Wärmeplanung 2025
Begleitdokument zum KWW-Technikkatalog Wärmeplanung:
Im Begleitdokument zum KWW-Technikkatalog finden Sie weitere Hintergründe und Datenquellen. Das Dokument sowie ergänzende Informationen finden Sie auf der KWW-Website unter:
https://www.kww-halle.de/service/infothek/detail/kww-technikkatalog-waermeplanung-begleitdokument
Autorinnen und Autoren:
Jana Bosse, Aljoscha Fahning, Valentin Fried, Daniel Jessen, Kristian Prewitz, Robert Schönnagel
| Technologie | Kompressionswärmepumpe Abwärme (zentral)
| Jahr | 2025
| Technische Daten | Einheit | 0,3 | 1 | 2 | 5 | 10 | 20 | Unsicherheit ± | Quellen | Anmerkungen
| Thermische Leistung | MWth | 0.3 | 1 | 2 | 5 | 10 | 20
| Jahresarbeitszahl | - | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 10% | [12], [29] | CA, CH
| Lebensdauer | a | 25 | 25 | 25 | 25 | 25 | 25 | 50% | [12] | CD
| Kosten (€/2025 real, ohne MwSt.) | Einheit
| Spezifische Investitionskosten | €/kWth | 1770 | 1300 | 1080 | 850 | 710 | 590 | 30% | [12], [29] | CA, CC
| davon Anlagenkosten | % | 75 | 77 | 78 | 80 | 80 | 80 | 5% | [12], [29]
| davon Installationskosten | % | 25 | 23 | 22 | 20 | 20 | 20 | 5% | [12], [29]
| Investitionskosten gesamt | € | 531000 | 1300000 | 2160000 | 4250000 | 7100000 | 11800000 | 30% | [12], [29] | CA, CC
| erwartete Änderung bis 2030 | % | -5 | -5 | -5 | -5 | -5 | -5 |  | [12] | CE
| erwartete Änderung bis 2040 | % | -10 | -10 | -10 | -10 | -10 | -10 |  | [12] | CE
| Jährliche Fixkosten O&M | €/a | 15000 | 35700 | 58900 | 114200 | 188500 | 311000 | 30% | [12], [29] | CI
| Variable Kosten O&M | €/MWhth | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 50% | [28]
| Kostenkurve | Investitionskosten gesamt [€] = a*Leistung [kWth]^b
| Jahr | 2025 | 2030 | 2040
| Parameter a | 7898 | 7503.1 | 7108.2
| Parameter b | 0.74 | 0.74 | 0.74
Anmerkungen
| CA | Die tatsächliche Weiterentwicklung bei der Optimierung der Leistungszahl und Investitionskosten hängt von der Entwicklung der Kraftstoff- und Strompreise ab (vgl. [12]).
| CC | Preisspanne auch abhängig von der Vorlauftemperatur Tmax, da die Komponenten der Wärmepumpe für höhere Temperaturen (bzw. Druckstufen) ausgelegt werden müssen (vgl. [12]).
| CD | Die Lebensdauer kann zwischen 15 und 40 Jahren liegen (vgl. [12]).
| CE | Kostenminderung nach [12] plausibel durch erwarteten technischen Fortschritt und Markthochlauf.
| CH | Typische JAZ von realisierten Anlagen. Die JAZ ist abhängig von der Vor-/Rücklauftemperatur des Wärmenetzes (vgl. [12]). Für die hier dargestellte Preiskurve kann von einer durchschnittlichen TQuelle = 15 °C und einer TSenke = 80 °C ausgegangen werden; die Referenzanlagen liegen hierbei jedoch weit auseinander.
| CI | Näherungsweise interpoliert aus [12].
Quellen
| [12] | Langreder et al. (2024): Technikkatalog Wärmeplanung (Version 1.1).
| [28] | Klimaschutz- und Energieagentur Baden-Württemberg (KEA-BW, 2024): Technikkatalog Baden-Württemberg (Version 1.1), Tabellenblatt 2.3: Zentrale Wärmeversorgung - Groß-Wärmepumpen.
| [29] | Praxiserfahrung von Ramboll.